## Sheet1
| Parameters | Values | Limit | Units
0 | Rating | [15.] |  | MW
1 | Air gap diameter | [12.77695918] |  | m
2 | Overall Outer diameter | [13.58010819] |  | m
3 | Stator length | [2.22179429] |  | m
4 | l/d ratio | [0.17389069] | (0.15-0.3)
5 | Slot_aspect_ratio | [4.7043168] | (4-10)
6 | Pole pitch | [133.80000368] |  | mm
7 | Slot pitch | [111.27700306] |  | mm
8 | Stator slot height | [119.55280039] |  | mm
9 | Stator slotwidth | [25.41342464] |  | mm
10 | Stator tooth width | [85.35035488] |  | mm
11 | Stator tooth height | [128.55181693] |  | mm
12 | Stator yoke height | [202.24313529] |  | mm
13 | Rotor yoke height | [102.62617096] |  | mm
14 | Magnet height | [150.] |  | mm
15 | Magnet width | [107.04000294] |  | mm
16 | Peak air gap flux density fundamental | [0.90341775] | <2 | T
17 | Peak stator yoke flux density | [0.19125858] | <2 | T
18 | Peak rotor yoke flux density | [0.37690908] | <2 | T
19 | Flux density above magnet | [1.09396912] |  | T
20 | Maximum Stator flux density | [0.00896305] | <2 | T
21 | Maximum tooth flux density | [1.17784654] | <2 | T
22 | Pole pairs | [150.] |  | -
23 | Generator output frequency | [18.84711565] |  | Hz
24 | Generator output phase voltage | [6398.78937703] | 500<E_p<10000 | V
25 | Generator Output phase current | [782.87532947] |  | A
26 | Stator resistance | [0.34108659] |  | ohm/phase
27 | Synchronous inductance | [0.0119989] |  | p.u
28 | Stator slots | [360.] |  | slots
29 | Stator turns | [480.] |  | turns
30 | Conductor cross-section | [168.53678235] |  | mm^2
31 | Stator Current density | [4.64513039] | 3-6 | A/mm^2
32 | Specific current loading | [56.28299167] | 60 | kA/m
33 | Generator Efficiency | [94.00000978] | >=95.4 | %
34 | Iron mass | [273.88029169] |  | tons
35 | Magnet mass | [81.60147433] |  | tons
36 | Copper mass | [10.26513731] |  | tons
37 | Structural Mass | [227.88941101] |  | tons
38 | ************************** | ************************ | ************************ | ************
39 | Stator spokes (n_s) | 5
40 | Stator arm depth (d_s) | [498.94833431] |  | mm
41 | Circumferential arm depth (b_st) | [968.94833431] | [1382.30076758] | mm
42 | Spoke arm thickness (t_ws) | [108.94833431] |  | mm
43 | Rotor spokes (n_r) | 5
44 | Rotor arm depth (d_r) | [498.94833431] |  | mm
45 | Circumferential arm depth (b_r) | [1198.94833431] | [1884.95559215] | mm
46 | Spoke arm thickness (t_wr) | [58.94833431] |  | mm
47 | Rotor rim thickness | [148.94833431] |  | mm
48 | Stator rim thickness | [40.] |  | mm
49 | Rotor radial deflection | [0.505] | [0.51107837] | mm
50 | Rotor axial deflection | [12.27755813] | [22.21794287] | mm
51 | Rotor twist | [5.39282304] | [5.92544002] | deg
52 | Torsional Constraint | [1.]
53 | Stator radial deflection | [0.4457437] | [0.51107837] | mm
54 | Stator axial deflection | [9.02603651] | [22.21794287] | mm
55 | Stator twist | [5.08017439] | [5.2751771] | deg
56 | Torsional Constraint | [1.]
57 | ************************** | ************************** | ************************** | ************
58 | Total Mass | [593.63631433] |  | tons
59 | Total Material Cost | [8067.80792257] |  | k$