## Sheet1
| Parameters | Values | Limit | Units
0 | Rating | [15.] |  | MW
1 | Air gap diameter | [12.79338431] |  | m
2 | Overall Outer diameter | [13.39610198] |  | m
3 | Stator length | [2.22752629] |  | m
4 | l/d ratio | [0.17411548] | (0.15-0.3)
5 | Slot_aspect_ratio | [4.0033326] | (4-10)
6 | Pole pitch | [133.97200725] |  | mm
7 | Slot pitch | [111.4200527] |  | mm
8 | Stator slot height | [103.02714235] |  | mm
9 | Stator slotwidth | [25.73534416] |  | mm
10 | Stator tooth width | [85.17725378] |  | mm
11 | Stator tooth height | [112.02818238] |  | mm
12 | Stator yoke height | [192.16563754] |  | mm
13 | Rotor yoke height | [93.82356935] |  | mm
14 | Magnet height | [149.99167341] |  | mm
15 | Magnet width | [107.1776058] |  | mm
16 | Peak air gap flux density fundamental | [0.90331068] | <2 | T
17 | Peak stator yoke flux density | [0.20152339] | <2 | T
18 | Peak rotor yoke flux density | [0.41275205] | <2 | T
19 | Flux density above magnet | [1.09383947] |  | T
20 | Maximum Stator flux density | [0.0089287] | <2 | T
21 | Maximum tooth flux density | [1.18161739] | <2 | T
22 | Pole pairs | [150.] |  | -
23 | Generator output frequency | [18.84711565] |  | Hz
24 | Generator output phase voltage | [6422.78335997] | 500<E_p<10000 | V
25 | Generator Output phase current | [779.92442979] |  | A
26 | Stator resistance | [0.34318805] |  | ohm/phase
27 | Synchronous inductance | [0.01082321] |  | p.u
28 | Stator slots | [360.] |  | slots
29 | Stator turns | [480.] |  | turns
30 | Conductor cross-section | [167.90716923] |  | mm^2
31 | Stator Current density | [4.64497397] | 3-6 | A/mm^2
32 | Specific current loading | [55.99885557] | 60 | kA/m
33 | Generator Efficiency | [94.0539658] | >=95.4 | %
34 | Iron mass | [253.48751777] |  | tons
35 | Magnet mass | [81.91010525] |  | tons
36 | Copper mass | [10.251357] |  | tons
37 | Structural Mass | [313.91018112] |  | tons
38 | ************************** | ************************ | ************************ | ************
39 | Rotor disc thickness | [112.54359053] |  | mm
40 | Rotor rim thickness | [57.54359053] |  | mm
41 | Stator disc thickness | [127.54359053] |  | mm
42 | Stator rim thickness | [43.70431527] |  | mm
43 | Rotor radial deflection | [0.49306523] | [0.51173537] | mm
44 | Rotor axial deflection | [17.66066873] | [23.40069879] | mm
45 | Rotor twist | [0.00012077] | [0.05] | deg
46 | Torsional Constraint | [1.]
47 | Stator radial deflection | [0.2507439] | [0.51173537] | mm
48 | Stator axial deflection | [24.21646376] | [23.55069879] | mm
49 | Stator twist | [6.41325617e-05] | [0.05] | deg
50 | Torsional Constraint | [1.]
51 | ************************** | ************************** | ************************** | ************
52 | Total Mass | [659.55916115] |  | tons
53 | Total Material Cost | [8128.85347923] |  | k$