## Overview
Parameter | IEA 15 MW Reference Wind Turbine
Power rating [MW] | 15
Turbine class | IEC Class IB
Specific rating [W/m^2] | 331.5728
Rotor orientation | Upwind
Number of blades | 3
Control | Variable speed, Collective pitch
Cut-in wind speed [m/s] | 3
Rated wind speed [m/s] | 10.88
Cut-out wind speed [m/s] | 25
Rotor diameter [m] | 240
Airfoil series | FFA-W3
Hub height [m] | 150
Hub diameter [m] | 7.94
Hub distance from center to blades [m] | 3
Hub Overhang [m] | -11.014
Drive train | Low speed, Direct drive
Design tip speed ratio | 9
Minimum rotor speed [rpm] | 5
Maximum rotor speed [rpm] | 7.56
Maximum tip speed [m/s] | 95
Shaft tilt angle [deg] | 6
Rotor pre-cone angle [deg] | -4
Tower top to nacelle (yaw bearing height) [m] | 0.38
Tower top to shaft distance [m] | 4.348
Generator efficiency [%] | 0.93
Blade pre-bend [m] | 4
Blade mass [t] | 65.252
Hub mass [t] | 190
Generator mass [t] | 371.5917
Turret/Nose mass [t] | 11.394
Bedplate mass [t] | 70.329
Shaft mass [t] | 15.734
Shaft bearing mass (SRB) [t] | 5.664
Shaft bearing mass (TDO) [t] | 2.23
Flange mass [t] | 3.946
Yaw system mass [t] | 100
Other nacelle mass (electronics, thermal system, etc) [t] | 50
Nacelle mass [t] | 630.888
RNA mass [t] | 1016.645
Nacelle center of mass from tower top [m] | [-6.47601681, 0.0, 4.2691133]
Tower mass [t] | 859.8
Tower base diameter [m] | 10
Transition piece height [m] | 15
Monopile embedment depth [m] | 45
Monopile base diameter [m] | 10
Monopile mass [t] | 1317.7

## Blade Geometry
Spanwise position [r/R] | Airfoil name
0 | circular
0.02 | circular
0.15 | SNL-FFA-W3-500
0.24517 | FFA-W3-360
0.32884 | FFA-W3-330blend
0.43918 | FFA-W3-301
0.53767 | FFA-W3-270blend
0.63821 | FFA-W3-241
0.77174 | FFA-W3-211
1 | FFA-W3-211
Profile
Spanwise position [r/R] | Chord [m] | Twist [rad] | Pitch axis [x/c] | Span [m] | Prebend [m] | Sweep [m]
0 | 5.2 | 0.27218 | 0.50455 | 0 | 0 | 0
0.02 | 5.2083 | 0.27212 | 0.49036 | 2.34 | -0.017927 | 0
0.04 | 5.2357 | 0.26928 | 0.47345 | 4.68 | -0.041095 | 0
0.06 | 5.2889 | 0.26161 | 0.45518 | 7.02 | -0.069413 | 0
0.08 | 5.3606 | 0.25004 | 0.43618 | 9.36 | -0.10094 | 0
0.1 | 5.4433 | 0.23553 | 0.4174 | 11.7 | -0.13373 | 0
0.125 | 5.551 | 0.21468 | 0.39573 | 14.625 | -0.17354 | 0
0.15 | 5.6501 | 0.19255 | 0.37553 | 17.55 | -0.2085 | 0
0.16903 | 5.711 | 0.17599 | 0.36113 | 19.777 | -0.22951 | 0
0.18807 | 5.7521 | 0.16057 | 0.34875 | 22.004 | -0.24384 | 0
0.2071 | 5.7672 | 0.14712 | 0.33845 | 24.231 | -0.24981 | 0
0.22614 | 5.7551 | 0.13573 | 0.33037 | 26.4579 | -0.25029 | 0
0.24517 | 5.7023 | 0.12536 | 0.32401 | 28.6849 | -0.2494 | 0
0.26609 | 5.6009 | 0.11392 | 0.31865 | 31.1324 | -0.24749 | 0
0.28701 | 5.463 | 0.10289 | 0.31443 | 33.5798 | -0.24464 | 0
0.30793 | 5.3095 | 0.092403 | 0.31121 | 36.0273 | -0.24099 | 0
0.32884 | 5.1487 | 0.082631 | 0.30855 | 38.4747 | -0.23649 | 0
0.35091 | 4.991 | 0.073312 | 0.30618 | 41.0566 | -0.23153 | 0
0.37298 | 4.8498 | 0.065028 | 0.30374 | 43.6384 | -0.22318 | 0
0.39505 | 4.7276 | 0.057717 | 0.30096 | 46.2203 | -0.20501 | 0
0.41711 | 4.6047 | 0.050963 | 0.298 | 48.8021 | -0.17342 | 0
0.43918 | 4.4821 | 0.044698 | 0.29508 | 51.384 | -0.12433 | 0
0.45888 | 4.3738 | 0.039479 | 0.29285 | 53.6887 | -0.072349 | 0
0.47858 | 4.2673 | 0.034563 | 0.29099 | 55.9934 | -0.013809 | 0
0.49827 | 4.163 | 0.029908 | 0.28945 | 58.2981 | 0.049657 | 0
0.51797 | 4.0617 | 0.025446 | 0.28839 | 60.6028 | 0.11436 | 0
0.53767 | 3.9635 | 0.021216 | 0.28782 | 62.9076 | 0.18381 | 0
0.55778 | 3.8669 | 0.017242 | 0.28785 | 65.2601 | 0.26957 | 0
0.57789 | 3.773 | 0.013528 | 0.28799 | 67.6127 | 0.36837 | 0
0.59799 | 3.6813 | 0.010043 | 0.28876 | 69.9652 | 0.48161 | 0
0.6181 | 3.5907 | 0.0066352 | 0.28991 | 72.3177 | 0.60359 | 0
0.63821 | 3.5008 | 0.0032468 | 0.29157 | 74.6703 | 0.73337 | 0
0.65728 | 3.4151 | -3.3696e-05 | 0.29342 | 76.9023 | 0.8602 | 0
0.67636 | 3.3289 | -0.0035493 | 0.29557 | 79.1342 | 0.98957 | 0
0.69544 | 3.2415 | -0.0074216 | 0.29798 | 81.3662 | 1.1197 | 0
0.71451 | 3.1551 | -0.011929 | 0.3006 | 83.5981 | 1.2568 | 0
0.73359 | 3.0695 | -0.017137 | 0.30341 | 85.8301 | 1.4016 | 0
0.75267 | 2.984 | -0.022397 | 0.30632 | 88.0621 | 1.5532 | 0
0.77174 | 2.898 | -0.027491 | 0.30931 | 90.294 | 1.711 | 0
0.8 | 2.7682 | -0.0338 | 0.31364 | 93.6 | 1.9546 | 0
0.81875 | 2.6796 | -0.036799 | 0.3168 | 95.7938 | 2.1217 | 0
0.8375 | 2.5882 | -0.03781 | 0.32036 | 97.9875 | 2.2925 | 0
0.85625 | 2.4939 | -0.037988 | 0.32441 | 100.1813 | 2.4671 | 0
0.875 | 2.3974 | -0.037718 | 0.32881 | 102.375 | 2.648 | 0
0.89375 | 2.2986 | -0.036976 | 0.33352 | 104.5687 | 2.8349 | 0
0.9125 | 2.1977 | -0.03576 | 0.33847 | 106.7625 | 3.028 | 0
0.93125 | 2.0947 | -0.034059 | 0.34375 | 108.9562 | 3.2265 | 0
0.95 | 1.9898 | -0.03168 | 0.3495 | 111.15 | 3.4307 | 0
0.975 | 1.8481 | -0.027365 | 0.35827 | 114.075 | 3.7111 | 0
0.97863 | 1.8258 | -0.026626 | 0.35964 | 114.5 | 3.7525 | 0
0.98077 | 1.8121 | -0.026178 | 0.36046 | 114.75 | 3.777 | 0
0.98291 | 1.797 | -0.02572 | 0.36129 | 115 | 3.8015 | 0
0.98504 | 1.7793 | -0.025251 | 0.36213 | 115.25 | 3.8261 | 0
0.98718 | 1.7566 | -0.024773 | 0.36297 | 115.5 | 3.8508 | 0
0.98932 | 1.7239 | -0.024284 | 0.36382 | 115.75 | 3.8755 | 0
0.99145 | 1.6717 | -0.023785 | 0.36468 | 116 | 3.9003 | 0
0.99359 | 1.5813 | -0.023275 | 0.36554 | 116.25 | 3.9251 | 0
0.99573 | 1.4157 | -0.022755 | 0.36642 | 116.5 | 3.95 | 0
0.99786 | 1.1027 | -0.022225 | 0.3673 | 116.75 | 3.975 | 0
1 | 0.5 | -0.021684 | 0.36818 | 117 | 4 | 0

## Airfoil circular
name | circular
relative_thickness | 1
aerodynamic_center | 0.5
x | y
1 | 0
0.99901 | 0.0314
0.99606 | 0.06267
0.99114 | 0.09369
0.98429 | 0.12434
0.97553 | 0.15451
0.96489 | 0.18406
0.95241 | 0.21289
0.93815 | 0.24088
0.92216 | 0.26791
0.90451 | 0.29389
0.88526 | 0.31871
0.86448 | 0.34227
0.84227 | 0.36448
0.81871 | 0.38526
0.79389 | 0.40451
0.76791 | 0.42216
0.74088 | 0.43815
0.71289 | 0.45241
0.68406 | 0.46489
0.65451 | 0.47553
0.62434 | 0.48429
0.59369 | 0.49114
0.56267 | 0.49606
0.5314 | 0.49901
0.5 | 0.5
0.4686 | 0.49901
0.43733 | 0.49606
0.40631 | 0.49114
0.37566 | 0.48429
0.34549 | 0.47553
0.31594 | 0.46489
0.28711 | 0.45241
0.25912 | 0.43815
0.23209 | 0.42216
0.20611 | 0.40451
0.18129 | 0.38526
0.15773 | 0.36448
0.13552 | 0.34227
0.11474 | 0.31871
0.09549 | 0.29389
0.07784 | 0.26791
0.06185 | 0.24088
0.04759 | 0.21289
0.03511 | 0.18406
0.02447 | 0.15451
0.01571 | 0.12434
0.00886 | 0.09369
0.00394 | 0.06267
0.00099 | 0.0314
0 | 0
0.00099 | -0.0314
0.00394 | -0.06267
0.00886 | -0.09369
0.01571 | -0.12434
0.02447 | -0.15451
0.03511 | -0.18406
0.04759 | -0.21289
0.06185 | -0.24088
0.07784 | -0.26791
0.09549 | -0.29389
0.11474 | -0.31871
0.13552 | -0.34227
0.15773 | -0.36448
0.18129 | -0.38526
0.20611 | -0.40451
0.23209 | -0.42216
0.25912 | -0.43815
0.28711 | -0.45241
0.31594 | -0.46489
0.34549 | -0.47553
0.37566 | -0.48429
0.40631 | -0.49114
0.43733 | -0.49606
0.4686 | -0.49901
0.5 | -0.5
0.5314 | -0.49901
0.56267 | -0.49606
0.59369 | -0.49114
0.62434 | -0.48429
0.65451 | -0.47553
0.68406 | -0.46489
0.71289 | -0.45241
0.74088 | -0.43815
0.76791 | -0.42216
0.79389 | -0.40451
0.81871 | -0.38526
0.84227 | -0.36448
0.86448 | -0.34227
0.88526 | -0.31871
0.90451 | -0.29389
0.92216 | -0.26791
0.93815 | -0.24088
0.95241 | -0.21289
0.96489 | -0.18406
0.97553 | -0.15451
0.98429 | -0.12434
0.99114 | -0.09369
0.99606 | -0.06267
0.99901 | -0.0314
1 | 0
Reynolds | 3000000
alpha [rad] | c_l | c_d | c_m
-3.14 | 0.0001 | 0.35 | -0.0001
3.14 | 0.0001 | 0.35 | -0.0001

## Airfoil SNL-FFA-W3-500
name | SNL-FFA-W3-500
relative_thickness | 0.5
aerodynamic_center | 0.316
x | y
1 | 0.0105
0.99944 | 0.01087
0.99812 | 0.011745
0.99569 | 0.013341
0.9923 | 0.015549
0.98803 | 0.0183
0.98282 | 0.021606
0.97666 | 0.02544
0.96964 | 0.029739
0.96174 | 0.034482
0.95297 | 0.039649
0.94339 | 0.045193
0.93301 | 0.050916
0.92185 | 0.057083
0.90995 | 0.063581
0.89736 | 0.070427
0.88409 | 0.077347
0.87016 | 0.084671
0.85565 | 0.09218
0.84058 | 0.099901
0.82497 | 0.10757
0.80889 | 0.11534
0.79236 | 0.12314
0.77542 | 0.13106
0.75813 | 0.13881
0.7405 | 0.14656
0.72259 | 0.15414
0.70445 | 0.16162
0.68609 | 0.16908
0.66757 | 0.17622
0.64893 | 0.18309
0.63019 | 0.18987
0.6114 | 0.19625
0.5926 | 0.20235
0.57381 | 0.20832
0.55508 | 0.21376
0.53642 | 0.21903
0.51788 | 0.22393
0.49948 | 0.22836
0.48125 | 0.23243
0.46322 | 0.23603
0.44541 | 0.23923
0.42784 | 0.24207
0.41054 | 0.2444
0.39353 | 0.24633
0.37681 | 0.24781
0.36042 | 0.24908
0.34436 | 0.24962
0.32866 | 0.25
0.31332 | 0.24991
0.29835 | 0.2494
0.28377 | 0.24844
0.26957 | 0.24723
0.25577 | 0.24556
0.24238 | 0.24358
0.2294 | 0.24125
0.21682 | 0.2386
0.20466 | 0.23566
0.19291 | 0.23243
0.18157 | 0.22884
0.17066 | 0.22497
0.16015 | 0.22083
0.15006 | 0.2165
0.14035 | 0.21198
0.13107 | 0.20723
0.12216 | 0.20232
0.11366 | 0.19717
0.10554 | 0.19204
0.097791 | 0.18656
0.090429 | 0.18109
0.083416 | 0.17546
0.076774 | 0.16968
0.070469 | 0.16379
0.0645 | 0.15776
0.058882 | 0.1517
0.053568 | 0.14556
0.048576 | 0.13949
0.043898 | 0.13334
0.039495 | 0.12705
0.035395 | 0.12087
0.031576 | 0.11469
0.028006 | 0.10849
0.024716 | 0.10222
0.021681 | 0.095893
0.018863 | 0.089807
0.016295 | 0.083748
0.013966 | 0.077738
0.011818 | 0.071879
0.0098836 | 0.06601
0.0081837 | 0.060189
0.0066313 | 0.053909
0.0052485 | 0.047327
0.0040827 | 0.040149
0.00309 | 0.033726
0.002191 | 0.02591
0.0014597 | 0.020032
0.00096333 | 0.014812
0.00059878 | 0.010964
0.00028988 | 0.0051542
7.804e-05 | 0.0023778
0 | 0
7.807e-05 | -0.0067635
0.00029009 | -0.0092701
0.00059937 | -0.014853
0.00096448 | -0.019098
0.0014626 | -0.024252
0.0021966 | -0.03028
0.0030988 | -0.037492
0.0040952 | -0.043397
0.0052677 | -0.049743
0.0066584 | -0.055936
0.0082194 | -0.061913
0.0099309 | -0.067583
0.01188 | -0.073402
0.014045 | -0.079132
0.016392 | -0.084982
0.018985 | -0.090992
0.021829 | -0.096921
0.024893 | -0.10303
0.02822 | -0.10915
0.031829 | -0.11531
0.03569 | -0.12114
0.039842 | -0.12715
0.0443 | -0.1332
0.049038 | -0.13898
0.0541 | -0.14485
0.059487 | -0.15067
0.065188 | -0.15649
0.071248 | -0.16232
0.077646 | -0.16795
0.084397 | -0.17356
0.091523 | -0.17905
0.099007 | -0.18436
0.10689 | -0.18965
0.11515 | -0.19467
0.12381 | -0.19968
0.13287 | -0.20449
0.14233 | -0.20911
0.15221 | -0.21357
0.1625 | -0.2179
0.17321 | -0.2219
0.18434 | -0.22585
0.1959 | -0.22943
0.20788 | -0.23283
0.22029 | -0.23594
0.23312 | -0.23868
0.24637 | -0.24128
0.26004 | -0.24343
0.27412 | -0.24536
0.28861 | -0.24669
0.3035 | -0.24775
0.31877 | -0.24841
0.33443 | -0.2487
0.35046 | -0.24831
0.36684 | -0.24764
0.38356 | -0.24639
0.40061 | -0.24455
0.41796 | -0.24222
0.43559 | -0.23936
0.45349 | -0.23594
0.47163 | -0.23174
0.48999 | -0.22715
0.50854 | -0.22177
0.52725 | -0.21594
0.54609 | -0.20951
0.56503 | -0.20243
0.58405 | -0.19484
0.60309 | -0.18681
0.62214 | -0.17831
0.64115 | -0.16937
0.66008 | -0.16006
0.67891 | -0.15031
0.69757 | -0.14049
0.71604 | -0.13045
0.73429 | -0.12029
0.75225 | -0.1102
0.7699 | -0.10039
0.78719 | -0.090731
0.80407 | -0.081406
0.82051 | -0.072716
0.83647 | -0.064445
0.85189 | -0.056665
0.86675 | -0.04954
0.88101 | -0.042991
0.89461 | -0.037131
0.90752 | -0.031979
0.91973 | -0.027475
0.93118 | -0.023702
0.94183 | -0.020375
0.95168 | -0.017994
0.96067 | -0.01593
0.96879 | -0.014214
0.97601 | -0.012838
0.98233 | -0.011777
0.98769 | -0.010999
0.99209 | -0.010451
0.99557 | -0.010082
0.99806 | -0.0098546
0.99943 | -0.0097435
1 | -0.0097
Reynolds | 8100000
alpha [rad] | c_l | c_d | c_m
-3.141 | 0 | 0.0844 | 0
-2.9671 | 0.4419 | 0.0844 | 0.3125
-2.7925 | 0.8837 | 0.1268 | 0.2831
-2.618 | 0.9674 | 0.2927 | 0.2632
-2.4435 | 0.7801 | 0.497 | 0.2048
-2.2689 | 0.6293 | 0.7161 | 0.1932
-2.0944 | 0.4785 | 0.9246 | 0.2008
-1.9199 | 0.3189 | 1.0985 | 0.2136
-1.7453 | 0.1553 | 1.2182 | 0.2221
-1.5708 | 0 | 1.2707 | 0.2198
-1.3963 | -0.1553 | 1.2182 | 0.196
-1.2217 | -0.3189 | 1.0985 | 0.1635
-1.0472 | -0.4784 | 0.9246 | 0.1285
-0.87266 | -0.6293 | 0.7161 | 0.0965
-0.69813 | -0.7801 | 0.497 | 0.0716
-0.5236 | -0.9674 | 0.2927 | 0.0522
-0.34907 | -1.0281 | 0.1499 | -0.0063
-0.3447 | -1.0243 | 0.1472 | -0.0089
-0.33598 | -1.0052 | 0.1447 | -0.0099
-0.33161 | -0.9971 | 0.1433 | -0.0105
-0.32725 | -1.0052 | 0.1403 | -0.011
-0.32289 | -0.9995 | 0.1386 | -0.0116
-0.31852 | -0.9908 | 0.1373 | -0.012
-0.31416 | -0.9815 | 0.136 | -0.0126
-0.30543 | -0.9764 | 0.1322 | -0.0135
-0.30107 | -0.9705 | 0.1306 | -0.0139
-0.29671 | -0.9655 | 0.129 | -0.0143
-0.29234 | -0.9662 | 0.1268 | -0.0147
-0.28798 | -0.9544 | 0.1258 | -0.0151
-0.28362 | -0.9444 | 0.1246 | -0.0155
-0.27925 | -0.9405 | 0.1229 | -0.0158
-0.27489 | -0.9433 | 0.1206 | -0.0161
-0.27053 | -0.933 | 0.1195 | -0.0164
-0.26616 | -0.9211 | 0.1185 | -0.0168
-0.25744 | -0.9158 | 0.115 | -0.0173
-0.25307 | -0.907 | 0.1138 | -0.0175
-0.24871 | -0.8959 | 0.1127 | -0.0178
-0.24435 | -0.8926 | 0.111 | -0.0181
-0.23998 | -0.8808 | 0.11 | -0.0184
-0.23562 | -0.8722 | 0.1089 | -0.0186
-0.23126 | -0.866 | 0.1075 | -0.0188
-0.22689 | -0.8626 | 0.1059 | -0.0188
-0.22253 | -0.8489 | 0.1051 | -0.0192
-0.21817 | -0.8363 | 0.1042 | -0.0194
-0.2138 | -0.8363 | 0.1023 | -0.0194
-0.20944 | -0.8271 | 0.1013 | -0.0196
-0.20508 | -0.8141 | 0.1004 | -0.0198
-0.20071 | -0.8004 | 0.0997 | -0.02
-0.19199 | -0.789 | 0.0971 | -0.0199
-0.18762 | -0.7862 | 0.0956 | -0.0196
-0.18326 | -0.7747 | 0.0948 | -0.0194
-0.1789 | -0.7701 | 0.094 | -0.0184
-0.17453 | -0.7674 | 0.0925 | -0.0183
-0.17017 | -0.7506 | 0.0917 | -0.0192
-0.16581 | -0.729 | 0.0912 | -0.0205
-0.16144 | -0.7095 | 0.0902 | -0.0224
-0.15708 | -0.6855 | 0.0895 | -0.0247
-0.15272 | -0.659 | 0.0891 | -0.0267
-0.14835 | -0.6319 | 0.0887 | -0.0287
-0.14399 | -0.6019 | 0.0879 | -0.032
-0.13963 | -0.5718 | 0.0875 | -0.0345
-0.13526 | -0.5424 | 0.0873 | -0.0367
-0.1309 | -0.5098 | 0.0868 | -0.0399
-0.12654 | -0.4767 | 0.0864 | -0.043
-0.12217 | -0.4454 | 0.0862 | -0.0453
-0.11781 | -0.4142 | 0.086 | -0.0476
-0.11345 | -0.3791 | 0.0856 | -0.051
-0.10908 | -0.346 | 0.0853 | -0.0538
-0.10472 | -0.3144 | 0.0852 | -0.056
-0.10036 | -0.2817 | 0.085 | -0.0586
-0.09599 | -0.2461 | 0.0847 | -0.0619
-0.09163 | -0.2133 | 0.0846 | -0.0644
-0.08727 | -0.1827 | 0.0845 | -0.0663
-0.0829 | -0.1494 | 0.0843 | -0.0688
-0.07854 | -0.1158 | 0.0842 | -0.0715
-0.07418 | -0.0837 | 0.084 | -0.0737
-0.06981 | -0.0529 | 0.084 | -0.0756
-0.06545 | -0.0225 | 0.0839 | -0.0774
-0.06109 | 0.0089 | 0.0838 | -0.0793
-0.05672 | 0.0392 | 0.0838 | -0.0811
-0.05236 | 0.0686 | 0.0838 | -0.0826
-0.048 | 0.0974 | 0.0838 | -0.0838
-0.04363 | 0.126 | 0.0838 | -0.0852
-0.03927 | 0.1555 | 0.0838 | -0.0867
-0.03491 | 0.1853 | 0.0838 | -0.0883
-0.03054 | 0.2146 | 0.0837 | -0.0897
-0.02618 | 0.243 | 0.0837 | -0.091
-0.02182 | 0.2713 | 0.0838 | -0.0921
-0.01745 | 0.3006 | 0.0838 | -0.0936
-0.01309 | 0.3295 | 0.0838 | -0.0949
-0.00873 | 0.3578 | 0.0838 | -0.0961
-0.00436 | 0.3857 | 0.0838 | -0.0972
0 | 0.4135 | 0.0838 | -0.0983
0.00401 | 0.4425 | 0.0839 | -0.0995
0.0082 | 0.4715 | 0.0839 | -0.1008
0.01222 | 0.5003 | 0.0839 | -0.1019
0.01641 | 0.5286 | 0.084 | -0.1029
0.02042 | 0.5567 | 0.084 | -0.104
0.02443 | 0.585 | 0.0841 | -0.105
0.02862 | 0.6135 | 0.0841 | -0.1061
0.03264 | 0.6417 | 0.0842 | -0.1072
0.03683 | 0.6697 | 0.0842 | -0.1082
0.04084 | 0.6975 | 0.0843 | -0.1091
0.04485 | 0.7251 | 0.0843 | -0.11
0.04904 | 0.7528 | 0.0844 | -0.1109
0.05306 | 0.7807 | 0.0845 | -0.1119
0.05725 | 0.8083 | 0.0846 | -0.1128
0.06126 | 0.8358 | 0.0846 | -0.1137
0.06528 | 0.8631 | 0.0847 | -0.1146
0.06946 | 0.8902 | 0.0847 | -0.1153
0.07348 | 0.9173 | 0.0848 | -0.1161
0.07767 | 0.9444 | 0.0849 | -0.117
0.08168 | 0.9713 | 0.085 | -0.1178
0.0857 | 0.9981 | 0.0851 | -0.1185
0.08988 | 1.0249 | 0.0852 | -0.1192
0.0939 | 1.0515 | 0.0853 | -0.1199
0.09809 | 1.0779 | 0.0853 | -0.1206
0.1021 | 1.1041 | 0.0854 | -0.1212
0.10612 | 1.1302 | 0.0856 | -0.1218
0.1103 | 1.156 | 0.0857 | -0.1224
0.11432 | 1.1818 | 0.0858 | -0.123
0.11851 | 1.2076 | 0.0859 | -0.1235
0.12252 | 1.2334 | 0.086 | -0.124
0.12654 | 1.2589 | 0.0861 | -0.1245
0.13073 | 1.2841 | 0.0862 | -0.125
0.13474 | 1.3088 | 0.0864 | -0.1254
0.13893 | 1.3331 | 0.0865 | -0.1257
0.14294 | 1.357 | 0.0867 | -0.1259
0.14696 | 1.381 | 0.0869 | -0.1262
0.15115 | 1.4054 | 0.087 | -0.1265
0.15516 | 1.4295 | 0.0871 | -0.1267
0.15917 | 1.4531 | 0.0873 | -0.127
0.17244 | 1.5154 | 0.0879 | -0.1265
0.1857 | 1.5749 | 0.0886 | -0.1256
0.19897 | 1.6151 | 0.0895 | -0.1214
0.21206 | 1.6443 | 0.0912 | -0.1163
0.22532 | 1.6824 | 0.093 | -0.1133
0.23859 | 1.7146 | 0.0954 | -0.1107
0.25168 | 1.7362 | 0.0989 | -0.108
0.26494 | 1.7627 | 0.1024 | -0.1063
0.27821 | 1.7706 | 0.1076 | -0.1042
0.2913 | 1.7639 | 0.1144 | -0.1025
0.30456 | 1.7604 | 0.1211 | -0.1013
0.31782 | 1.7251 | 0.131 | -0.1001
0.33109 | 1.7035 | 0.1399 | -0.0998
0.34418 | 1.6784 | 0.1492 | -0.1001
0.35744 | 1.6505 | 0.1591 | -0.1016
0.37071 | 1.6227 | 0.1691 | -0.1036
0.3838 | 1.6067 | 0.1778 | -0.1064
0.39706 | 1.5972 | 0.1858 | -0.1099
0.41033 | 1.5892 | 0.1937 | -0.1136
0.42342 | 1.5815 | 0.2014 | -0.118
0.43668 | 1.5563 | 0.2135 | -0.1249
0.44995 | 1.5272 | 0.2267 | -0.1325
0.46304 | 1.4982 | 0.2399 | -0.14
0.4763 | 1.4691 | 0.2531 | -0.1476
0.48956 | 1.4401 | 0.2663 | -0.1551
0.50283 | 1.411 | 0.2795 | -0.1627
0.51592 | 1.382 | 0.2927 | -0.1703
0.52918 | 1.3622 | 0.3078 | -0.174
0.54245 | 1.3424 | 0.323 | -0.1777
0.55554 | 1.3225 | 0.3381 | -0.1815
0.5688 | 1.3027 | 0.3532 | -0.1852
0.58207 | 1.2829 | 0.3684 | -0.1889
0.59516 | 1.2631 | 0.3835 | -0.1926
0.60842 | 1.2433 | 0.3987 | -0.1964
0.62169 | 1.2234 | 0.4138 | -0.2001
0.63495 | 1.2036 | 0.4289 | -0.2039
0.64804 | 1.1838 | 0.4441 | -0.2076
0.66131 | 1.164 | 0.4592 | -0.2113
0.67457 | 1.1442 | 0.4743 | -0.215
0.68766 | 1.1243 | 0.4895 | -0.2188
0.70092 | 1.1064 | 0.5052 | -0.2218
0.71419 | 1.0905 | 0.5214 | -0.2242
0.72728 | 1.0745 | 0.5376 | -0.2266
0.74054 | 1.0586 | 0.5538 | -0.2289
0.75381 | 1.0426 | 0.5701 | -0.2313
0.7669 | 1.0267 | 0.5863 | -0.2337
0.78016 | 1.0107 | 0.6025 | -0.2361
0.79343 | 0.9948 | 0.6188 | -0.2384
0.80669 | 0.9788 | 0.635 | -0.2408
0.81978 | 0.9628 | 0.6512 | -0.2432
0.83305 | 0.9469 | 0.6675 | -0.2455
0.84631 | 0.9309 | 0.6837 | -0.2479
0.8594 | 0.915 | 0.6999 | -0.2503
0.87266 | 0.899 | 0.7161 | -0.2527
1.0472 | 0.6836 | 0.9246 | -0.2833
1.2217 | 0.4556 | 1.0985 | -0.3156
1.3963 | 0.2219 | 1.2182 | -0.3482
1.5708 | 0 | 1.2707 | -0.3773
1.7453 | -0.1553 | 1.2182 | -0.3877
1.9199 | -0.3189 | 1.0985 | -0.3865
2.0944 | -0.4784 | 0.9246 | -0.3806
2.2689 | -0.6293 | 0.7161 | -0.3803
2.4435 | -0.7801 | 0.497 | -0.4032
2.618 | -0.9674 | 0.2927 | -0.4854
2.7925 | -0.8837 | 0.1268 | -0.5325
2.9671 | -0.4418 | 0.0844 | -0.3906
3.141 | 0 | 0.0844 | 0

## Airfoil FFA-W3-211
name | FFA-W3-211
relative_thickness | 0.211
aerodynamic_center | 0.25
x | y
1 | 0.00094
0.99944 | 0.0010306
0.99812 | 0.0012464
0.99569 | 0.001644
0.9923 | 0.0022029
0.98803 | 0.0029141
0.98282 | 0.0037895
0.97666 | 0.0048332
0.96964 | 0.0060382
0.96174 | 0.007408
0.95297 | 0.0089448
0.94339 | 0.01064
0.93301 | 0.012524
0.92185 | 0.014572
0.90995 | 0.016797
0.89736 | 0.01918
0.88409 | 0.021743
0.87016 | 0.024455
0.85565 | 0.02735
0.84058 | 0.030383
0.82497 | 0.033558
0.80889 | 0.036877
0.79236 | 0.040346
0.77542 | 0.043947
0.75813 | 0.047663
0.7405 | 0.051486
0.72259 | 0.055408
0.70445 | 0.059358
0.68609 | 0.063388
0.66757 | 0.0674
0.64893 | 0.07143
0.63019 | 0.075418
0.6114 | 0.079381
0.5926 | 0.08322
0.57381 | 0.086949
0.55508 | 0.090537
0.53642 | 0.093994
0.51788 | 0.097297
0.49948 | 0.10037
0.48125 | 0.10331
0.46322 | 0.10607
0.44541 | 0.10853
0.42784 | 0.11081
0.41054 | 0.11273
0.39353 | 0.11447
0.37681 | 0.1159
0.36042 | 0.11703
0.34436 | 0.11783
0.32866 | 0.11838
0.31332 | 0.11853
0.29835 | 0.11842
0.28377 | 0.11789
0.26957 | 0.11713
0.25577 | 0.1161
0.24238 | 0.11482
0.2294 | 0.11325
0.21682 | 0.11141
0.20466 | 0.10943
0.19291 | 0.10729
0.18157 | 0.10496
0.17066 | 0.10246
0.16015 | 0.099935
0.15006 | 0.097204
0.14035 | 0.094413
0.13107 | 0.091569
0.12216 | 0.088633
0.11366 | 0.085645
0.10554 | 0.082602
0.097791 | 0.079541
0.090429 | 0.076474
0.083416 | 0.073383
0.076774 | 0.070292
0.070469 | 0.067199
0.0645 | 0.064114
0.058882 | 0.06106
0.053568 | 0.058025
0.048576 | 0.055034
0.043898 | 0.052079
0.039495 | 0.049149
0.035395 | 0.046271
0.031576 | 0.043449
0.028006 | 0.040662
0.024716 | 0.037958
0.021681 | 0.035308
0.018863 | 0.032692
0.016295 | 0.030158
0.013966 | 0.027684
0.011818 | 0.025257
0.0098836 | 0.022918
0.0081837 | 0.020654
0.0066313 | 0.01839
0.0052485 | 0.016327
0.0040827 | 0.014336
0.00309 | 0.012279
0.002191 | 0.010002
0.0014597 | 0.0071011
0.00096333 | 0.0046218
0.00059878 | 0.0027598
0.00028988 | 0.0012629
7.804e-05 | 0.00032267
0 | 0
7.807e-05 | -0.00031745
0.00029009 | -0.0011951
0.00059937 | -0.0024997
0.00096448 | -0.0040402
0.0014626 | -0.006058
0.0021966 | -0.0086106
0.0030988 | -0.010647
0.0040952 | -0.0123
0.0052677 | -0.013889
0.0066584 | -0.015424
0.0082194 | -0.016913
0.0099309 | -0.018543
0.01188 | -0.020297
0.014045 | -0.022061
0.016392 | -0.023835
0.018985 | -0.025713
0.021829 | -0.027644
0.024893 | -0.029602
0.02822 | -0.03163
0.031829 | -0.03371
0.03569 | -0.035826
0.039842 | -0.037993
0.0443 | -0.040207
0.049038 | -0.042453
0.0541 | -0.044738
0.059487 | -0.047051
0.065188 | -0.049389
0.071248 | -0.051769
0.077646 | -0.054171
0.084397 | -0.056588
0.091523 | -0.059015
0.099007 | -0.06144
0.10689 | -0.063866
0.11515 | -0.066273
0.12381 | -0.068648
0.13287 | -0.070998
0.14233 | -0.073294
0.15221 | -0.075545
0.1625 | -0.077734
0.17321 | -0.079826
0.18434 | -0.081825
0.1959 | -0.083709
0.20788 | -0.085448
0.22029 | -0.087035
0.23312 | -0.088466
0.24637 | -0.089717
0.26004 | -0.090753
0.27412 | -0.091577
0.28861 | -0.092161
0.3035 | -0.092458
0.31877 | -0.092474
0.33443 | -0.092163
0.35046 | -0.091493
0.36684 | -0.090468
0.38356 | -0.089039
0.40061 | -0.087207
0.41796 | -0.08496
0.43559 | -0.082262
0.45349 | -0.079111
0.47163 | -0.075502
0.48999 | -0.071475
0.50854 | -0.067052
0.52725 | -0.06234
0.54609 | -0.057432
0.56503 | -0.052357
0.58405 | -0.047189
0.60309 | -0.041968
0.62214 | -0.036815
0.64115 | -0.031776
0.66008 | -0.026925
0.67891 | -0.022307
0.69757 | -0.01798
0.71604 | -0.013981
0.73429 | -0.010324
0.75225 | -0.0070375
0.7699 | -0.004116
0.78719 | -0.0015575
0.80407 | 0.00059313
0.82051 | 0.002356
0.83647 | 0.0037555
0.85189 | 0.0048154
0.86675 | 0.0055336
0.88101 | 0.005958
0.89461 | 0.0060995
0.90752 | 0.0059969
0.91973 | 0.0056572
0.93118 | 0.0051348
0.94183 | 0.0044718
0.95168 | 0.0037738
0.96067 | 0.0030995
0.96879 | 0.0024577
0.97601 | 0.0018566
0.98233 | 0.001306
0.98769 | 0.00082003
0.99209 | 0.00040675
0.99557 | 6.986e-05
0.99806 | -0.00017578
0.99943 | -0.00031253
1 | -0.00037
Reynolds | 10000000
alpha [rad] | c_l | c_d | c_m
-3.14 | 0 | 0.024641 | 0
-3.1017 | 0.054025 | 0.025338 | 0.091429
-3.0618 | 0.10805 | 0.027424 | 0.18286
-3.0219 | 0.16208 | 0.030885 | 0.27429
-2.982 | 0.2161 | 0.035699 | 0.36571
-2.9421 | 0.27013 | 0.055991 | 0.39192
-2.9022 | 0.32415 | 0.081435 | 0.37898
-2.8623 | 0.37818 | 0.11112 | 0.36605
-2.8224 | 0.4322 | 0.14485 | 0.35312
-2.7826 | 0.48623 | 0.18242 | 0.34768
-2.7427 | 0.54025 | 0.22359 | 0.36471
-2.7028 | 0.59428 | 0.2681 | 0.38175
-2.6629 | 0.6483 | 0.31566 | 0.39878
-2.623 | 0.70233 | 0.36597 | 0.41581
-2.5831 | 0.75635 | 0.41871 | 0.41955
-2.5108 | 0.73188 | 0.51941 | 0.42287
-2.4385 | 0.70655 | 0.62488 | 0.42632
-2.3662 | 0.6776 | 0.73293 | 0.43163
-2.2939 | 0.64333 | 0.8413 | 0.43694
-2.2216 | 0.60277 | 0.94773 | 0.44389
-2.1492 | 0.5555 | 1.05 | 0.45171
-2.0769 | 0.50156 | 1.146 | 0.45897
-2.0046 | 0.44131 | 1.2337 | 0.46448
-1.9323 | 0.37542 | 1.3113 | 0.46998
-1.86 | 0.30482 | 1.3771 | 0.47096
-1.7877 | 0.23063 | 1.4299 | 0.47101
-1.7154 | 0.15413 | 1.4684 | 0.46824
-1.6431 | 0.076754 | 1.492 | 0.46149
-1.5708 | 6.9389e-17 | 1.5 | 0.45474
-1.4985 | -0.076754 | 1.492 | 0.44026
-1.4262 | -0.15413 | 1.4684 | 0.42578
-1.3539 | -0.23063 | 1.4299 | 0.40821
-1.2816 | -0.30482 | 1.3771 | 0.38846
-1.2093 | -0.37542 | 1.3113 | 0.36815
-1.137 | -0.44131 | 1.2337 | 0.34519
-1.0647 | -0.50156 | 1.146 | 0.32223
-0.99234 | -0.5555 | 1.05 | 0.29864
-0.92004 | -0.60277 | 0.94773 | 0.27486
-0.84773 | -0.64333 | 0.8413 | 0.25128
-0.77542 | -0.6776 | 0.73293 | 0.2281
-0.70312 | -0.70655 | 0.62488 | 0.20491
-0.63081 | -0.73188 | 0.51941 | 0.15416
-0.55851 | -0.75635 | 0.41871 | 0.10137
-0.48869 | -0.85636 | 0.28691 | 0.06527
-0.41888 | -1.1829 | 0.1396 | 0.016474
-0.34907 | -1.236 | 0.083446 | -0.0035156
-0.31416 | -1.2254 | 0.065092 | -0.0067166
-0.27925 | -1.2048 | 0.048882 | -0.0088127
-0.24435 | -1.1833 | 0.034172 | -0.011009
-0.20944 | -1.1009 | 0.021325 | -0.022688
-0.17453 | -0.88209 | 0.013859 | -0.043967
-0.13963 | -0.62981 | 0.010754 | -0.057559
-0.10472 | -0.3767 | 0.0088158 | -0.067475
-0.069813 | -0.12177 | 0.0070218 | -0.076804
-0.034907 | 0.1281 | 0.0066305 | -0.08283
-0.017453 | 0.25192 | 0.0066436 | -0.085344
0 | 0.37535 | 0.0067006 | -0.087772
0.017453 | 0.49828 | 0.0068082 | -0.090106
0.034907 | 0.62052 | 0.0069786 | -0.092342
0.05236 | 0.742 | 0.0072031 | -0.094469
0.069813 | 0.86238 | 0.0075148 | -0.096463
0.087266 | 0.98114 | 0.0079585 | -0.09828
0.10472 | 1.0966 | 0.0087217 | -0.099773
0.12217 | 1.209 | 0.0096835 | -0.10095
0.13963 | 1.3168 | 0.01097 | -0.10163
0.15708 | 1.4221 | 0.012275 | -0.10207
0.17453 | 1.5236 | 0.013686 | -0.10213
0.19199 | 1.6199 | 0.015288 | -0.10174
0.20944 | 1.7094 | 0.017171 | -0.10087
0.22689 | 1.7868 | 0.019735 | -0.099364
0.24435 | 1.8429 | 0.023679 | -0.097199
0.2618 | 1.8531 | 0.03094 | -0.094098
0.27925 | 1.8095 | 0.043032 | -0.091439
0.31416 | 1.6603 | 0.077304 | -0.09242
0.34907 | 1.5615 | 0.11202 | -0.098707
0.41888 | 1.4333 | 0.18408 | -0.1177
0.48869 | 1.2906 | 0.27589 | -0.14566
0.55851 | 1.0805 | 0.41871 | -0.18266
0.63081 | 1.0455 | 0.51941 | -0.20913
0.70312 | 1.0094 | 0.62488 | -0.23534
0.77542 | 0.96801 | 0.73293 | -0.25784
0.84773 | 0.91904 | 0.8413 | -0.28035
0.92004 | 0.86109 | 0.94773 | -0.30163
0.99234 | 0.79357 | 1.05 | -0.32226
1.0647 | 0.71651 | 1.146 | -0.34247
1.137 | 0.63044 | 1.2337 | -0.36135
1.2093 | 0.53632 | 1.3113 | -0.38024
1.2816 | 0.43546 | 1.3771 | -0.39704
1.3539 | 0.32947 | 1.4299 | -0.41341
1.4262 | 0.22019 | 1.4684 | -0.42844
1.4985 | 0.10965 | 1.492 | -0.44159
1.5708 | 9.7145e-17 | 1.5 | -0.45474
1.6431 | -0.076754 | 1.492 | -0.46149
1.7154 | -0.15413 | 1.4684 | -0.46824
1.7877 | -0.23063 | 1.4299 | -0.47101
1.86 | -0.30482 | 1.3771 | -0.47096
1.9323 | -0.37542 | 1.3113 | -0.46998
2.0046 | -0.44131 | 1.2337 | -0.46448
2.0769 | -0.50156 | 1.146 | -0.45897
2.1492 | -0.5555 | 1.05 | -0.45171
2.2216 | -0.60277 | 0.94773 | -0.44389
2.2939 | -0.64333 | 0.8413 | -0.43694
2.3662 | -0.6776 | 0.73293 | -0.43163
2.4385 | -0.70655 | 0.62488 | -0.42632
2.5108 | -0.73188 | 0.51941 | -0.42287
2.5831 | -0.75635 | 0.41871 | -0.41955
2.623 | -0.70233 | 0.36597 | -0.41581
2.6629 | -0.6483 | 0.31566 | -0.39878
2.7028 | -0.59428 | 0.2681 | -0.38175
2.7427 | -0.54025 | 0.22359 | -0.36471
2.7826 | -0.48623 | 0.18242 | -0.34768
2.8224 | -0.4322 | 0.14485 | -0.37026
2.8623 | -0.37818 | 0.11112 | -0.40605
2.9022 | -0.32415 | 0.081435 | -0.44184
2.9421 | -0.27013 | 0.055991 | -0.47763
2.982 | -0.2161 | 0.035699 | -0.45714
3.0219 | -0.16208 | 0.030885 | -0.34286
3.0618 | -0.10805 | 0.027424 | -0.22857
3.1017 | -0.054025 | 0.025338 | -0.11429
3.14 | 4.8572e-18 | 0.024641 | 0

## Airfoil FFA-W3-241
name | FFA-W3-241
relative_thickness | 0.241
aerodynamic_center | 0.25
x | y
1 | 0.00425
0.99944 | 0.0043621
0.99812 | 0.0046283
0.99569 | 0.005117
0.9923 | 0.0057996
0.98803 | 0.0066615
0.98282 | 0.0077128
0.97666 | 0.0089541
0.96964 | 0.010373
0.96174 | 0.011969
0.95297 | 0.013742
0.94339 | 0.015682
0.93301 | 0.017786
0.92185 | 0.020069
0.90995 | 0.022517
0.89736 | 0.025138
0.88409 | 0.027909
0.87016 | 0.030849
0.85565 | 0.033936
0.84058 | 0.037164
0.82497 | 0.040529
0.80889 | 0.04401
0.79236 | 0.047617
0.77542 | 0.051327
0.75813 | 0.055123
0.7405 | 0.058994
0.72259 | 0.062934
0.70445 | 0.066901
0.68609 | 0.070883
0.66757 | 0.074867
0.64893 | 0.078835
0.63019 | 0.082754
0.6114 | 0.086614
0.5926 | 0.090373
0.57381 | 0.094025
0.55508 | 0.097549
0.53642 | 0.10093
0.51788 | 0.10415
0.49948 | 0.10719
0.48125 | 0.11006
0.46322 | 0.11271
0.44541 | 0.11515
0.42784 | 0.11735
0.41054 | 0.11932
0.39353 | 0.12103
0.37681 | 0.12249
0.36042 | 0.12368
0.34436 | 0.1246
0.32866 | 0.12524
0.31332 | 0.12561
0.29835 | 0.12567
0.28377 | 0.12547
0.26957 | 0.12499
0.25577 | 0.12424
0.24238 | 0.12324
0.2294 | 0.122
0.21682 | 0.12054
0.20466 | 0.11887
0.19291 | 0.11699
0.18157 | 0.11493
0.17066 | 0.11269
0.16015 | 0.1103
0.15006 | 0.10777
0.14035 | 0.10511
0.13107 | 0.10233
0.12216 | 0.09945
0.11366 | 0.09649
0.10554 | 0.093459
0.097791 | 0.090364
0.090429 | 0.087222
0.083416 | 0.084034
0.076774 | 0.080827
0.070469 | 0.077594
0.0645 | 0.074348
0.058882 | 0.07111
0.053568 | 0.067873
0.048576 | 0.064653
0.043898 | 0.061454
0.039495 | 0.05826
0.035395 | 0.055109
0.031576 | 0.051996
0.028006 | 0.048918
0.024716 | 0.045891
0.021681 | 0.042896
0.018863 | 0.039919
0.016295 | 0.037002
0.013966 | 0.034185
0.011818 | 0.031372
0.0098836 | 0.028611
0.0081837 | 0.026038
0.0066313 | 0.023429
0.0052485 | 0.020761
0.0040827 | 0.018305
0.00309 | 0.015951
0.002191 | 0.013271
0.0014597 | 0.010499
0.00096333 | 0.0074621
0.00059878 | 0.0045372
0.00028988 | 0.0020445
7.804e-05 | 0.00050657
0 | 0
7.807e-05 | -0.00049018
0.00029009 | -0.0018413
0.00059937 | -0.0038182
0.00096448 | -0.0060571
0.0014626 | -0.0087056
0.0021966 | -0.011229
0.0030988 | -0.013422
0.0040952 | -0.015344
0.0052677 | -0.017167
0.0066584 | -0.019096
0.0082194 | -0.021307
0.0099309 | -0.023514
0.01188 | -0.025799
0.014045 | -0.02816
0.016392 | -0.03054
0.018985 | -0.032969
0.021829 | -0.035491
0.024893 | -0.038075
0.02822 | -0.040726
0.031829 | -0.04346
0.03569 | -0.046232
0.039842 | -0.04907
0.0443 | -0.05197
0.049038 | -0.054909
0.0541 | -0.057904
0.059487 | -0.06095
0.065188 | -0.064025
0.071248 | -0.067128
0.077646 | -0.070244
0.084397 | -0.07337
0.091523 | -0.076491
0.099007 | -0.079596
0.10689 | -0.082683
0.11515 | -0.085719
0.12381 | -0.088705
0.13287 | -0.091617
0.14233 | -0.094438
0.15221 | -0.097166
0.1625 | -0.09977
0.17321 | -0.10224
0.18434 | -0.10454
0.1959 | -0.10669
0.20788 | -0.10863
0.22029 | -0.11037
0.23312 | -0.11188
0.24637 | -0.11314
0.26004 | -0.11415
0.27412 | -0.11487
0.28861 | -0.1153
0.3035 | -0.11538
0.31877 | -0.11513
0.33443 | -0.11451
0.35046 | -0.1135
0.36684 | -0.11208
0.38356 | -0.11023
0.40061 | -0.10793
0.41796 | -0.10519
0.43559 | -0.10198
0.45349 | -0.098298
0.47163 | -0.094141
0.48999 | -0.089522
0.50854 | -0.084473
0.52725 | -0.079057
0.54609 | -0.07331
0.56503 | -0.0673
0.58405 | -0.061093
0.60309 | -0.054771
0.62214 | -0.048425
0.64115 | -0.042138
0.66008 | -0.036008
0.67891 | -0.030127
0.69757 | -0.024575
0.71604 | -0.019421
0.73429 | -0.014701
0.75225 | -0.010454
0.7699 | -0.0067345
0.78719 | -0.0035584
0.80407 | -0.00093374
0.82051 | 0.0011792
0.83647 | 0.002846
0.85189 | 0.0040941
0.86675 | 0.0049525
0.88101 | 0.0054653
0.89461 | 0.0056196
0.90752 | 0.0054773
0.91973 | 0.0050471
0.93118 | 0.004404
0.94183 | 0.0036087
0.95168 | 0.0027081
0.96067 | 0.0018027
0.96879 | 0.00091285
0.97601 | 5.718e-05
0.98233 | -0.00074311
0.98769 | -0.0014613
0.99209 | -0.0020799
0.99557 | -0.0025891
0.99806 | -0.0029629
0.99943 | -0.003172
1 | -0.00326
Reynolds | 10000000
alpha [rad] | c_l | c_d | c_m
-3.14 | 0 | 0.011775 | 0
-3.1017 | 0.058178 | 0.012482 | 0.091429
-3.0618 | 0.11636 | 0.014599 | 0.18286
-3.0219 | 0.17453 | 0.018111 | 0.27429
-2.982 | 0.23271 | 0.022996 | 0.36571
-2.9421 | 0.29089 | 0.029224 | 0.39568
-2.9022 | 0.34907 | 0.05382 | 0.38876
-2.8623 | 0.40725 | 0.083794 | 0.38184
-2.8224 | 0.46542 | 0.11786 | 0.37492
-2.7826 | 0.5236 | 0.15581 | 0.37408
-2.7427 | 0.58178 | 0.1974 | 0.39148
-2.7028 | 0.63996 | 0.24237 | 0.40888
-2.6629 | 0.69814 | 0.29043 | 0.42628
-2.623 | 0.75631 | 0.34128 | 0.44368
-2.5831 | 0.81449 | 0.3946 | 0.44537
-2.5108 | 0.77925 | 0.49645 | 0.44436
-2.4385 | 0.74511 | 0.60319 | 0.4436
-2.3662 | 0.70881 | 0.71263 | 0.44609
-2.2939 | 0.66835 | 0.82249 | 0.44858
-2.2216 | 0.62253 | 0.93051 | 0.4537
-2.1492 | 0.5708 | 1.0345 | 0.4602
-2.0769 | 0.51307 | 1.1322 | 0.46633
-2.0046 | 0.44965 | 1.2218 | 0.4713
-1.9323 | 0.38115 | 1.3012 | 0.47627
-1.86 | 0.30846 | 1.369 | 0.47705
-1.7877 | 0.23266 | 1.4238 | 0.47695
-1.7154 | 0.15503 | 1.4643 | 0.47409
-1.6431 | 0.076979 | 1.4899 | 0.46732
-1.5708 | 6.9389e-17 | 1.5 | 0.46055
-1.4985 | -0.076979 | 1.4899 | 0.44509
-1.4262 | -0.15503 | 1.4643 | 0.42964
-1.3539 | -0.23266 | 1.4238 | 0.41125
-1.2816 | -0.30846 | 1.369 | 0.39081
-1.2093 | -0.38115 | 1.3012 | 0.36988
-1.137 | -0.44965 | 1.2218 | 0.34663
-1.0647 | -0.51307 | 1.1322 | 0.32339
-0.99234 | -0.5708 | 1.0345 | 0.29984
-0.92004 | -0.62253 | 0.93051 | 0.27618
-0.84773 | -0.66835 | 0.82249 | 0.2528
-0.77542 | -0.70881 | 0.71263 | 0.22992
-0.70312 | -0.74511 | 0.60319 | 0.20705
-0.63081 | -0.77925 | 0.49645 | 0.14561
-0.55851 | -0.81449 | 0.3946 | 0.081308
-0.48869 | -1.0778 | 0.22252 | 0.045917
-0.41888 | -1.1269 | 0.15159 | 0.01901
-0.34907 | -1.1448 | 0.096988 | 0.00063155
-0.31416 | -1.128 | 0.077435 | -0.0034225
-0.27925 | -1.0939 | 0.061222 | -0.0058652
-0.24435 | -1.0596 | 0.046672 | -0.0065213
-0.20944 | -1.0312 | 0.033022 | -0.0075541
-0.17453 | -0.93706 | 0.020269 | -0.022432
-0.13963 | -0.6738 | 0.011679 | -0.055829
-0.10472 | -0.40391 | 0.0091782 | -0.07159
-0.069813 | -0.14226 | 0.0083876 | -0.081225
-0.034907 | 0.1158 | 0.008105 | -0.08892
-0.017453 | 0.24382 | 0.0080825 | -0.092353
0 | 0.37113 | 0.0081278 | -0.095564
0.017453 | 0.49766 | 0.0082403 | -0.098568
0.034907 | 0.62334 | 0.0084182 | -0.10139
0.05236 | 0.74798 | 0.0086734 | -0.10403
0.069813 | 0.87137 | 0.0090086 | -0.10645
0.087266 | 0.9932 | 0.0094473 | -0.10863
0.10472 | 1.1133 | 0.0099783 | -0.11057
0.12217 | 1.2304 | 0.010702 | -0.11214
0.13963 | 1.345 | 0.011528 | -0.11337
0.15708 | 1.4541 | 0.012694 | -0.11396
0.17453 | 1.5591 | 0.013965 | -0.11403
0.19199 | 1.6578 | 0.015453 | -0.11336
0.20944 | 1.7483 | 0.017243 | -0.11187
0.22689 | 1.8267 | 0.019611 | -0.10935
0.24435 | 1.8883 | 0.022932 | -0.10606
0.2618 | 1.9258 | 0.027953 | -0.10238
0.27925 | 1.9272 | 0.036091 | -0.098869
0.31416 | 1.8006 | 0.065343 | -0.09497
0.34907 | 1.6309 | 0.10459 | -0.099957
0.41888 | 1.4334 | 0.19148 | -0.12589
0.48869 | 1.288 | 0.28629 | -0.15453
0.55851 | 1.1636 | 0.3946 | -0.18396
0.63081 | 1.1132 | 0.49645 | -0.21099
0.70312 | 1.0644 | 0.60319 | -0.23768
0.77542 | 1.0126 | 0.71263 | -0.25992
0.84773 | 0.95478 | 0.82249 | -0.28216
0.92004 | 0.88932 | 0.93051 | -0.30323
0.99234 | 0.81542 | 1.0345 | -0.32368
1.0647 | 0.73296 | 1.1322 | -0.3438
1.137 | 0.64236 | 1.2218 | -0.36292
1.2093 | 0.5445 | 1.3012 | -0.38204
1.2816 | 0.44065 | 1.369 | -0.39944
1.3539 | 0.33237 | 1.4238 | -0.41648
1.4262 | 0.22148 | 1.4643 | -0.43231
1.4985 | 0.10997 | 1.4899 | -0.44643
1.5708 | 9.7145e-17 | 1.5 | -0.46055
1.6431 | -0.076979 | 1.4899 | -0.46732
1.7154 | -0.15503 | 1.4643 | -0.47409
1.7877 | -0.23266 | 1.4238 | -0.47695
1.86 | -0.30846 | 1.369 | -0.47705
1.9323 | -0.38115 | 1.3012 | -0.47627
2.0046 | -0.44965 | 1.2218 | -0.4713
2.0769 | -0.51307 | 1.1322 | -0.46633
2.1492 | -0.5708 | 1.0345 | -0.4602
2.2216 | -0.62253 | 0.93051 | -0.4537
2.2939 | -0.66835 | 0.82249 | -0.44858
2.3662 | -0.70881 | 0.71263 | -0.44609
2.4385 | -0.74511 | 0.60319 | -0.4436
2.5108 | -0.77925 | 0.49645 | -0.44436
2.5831 | -0.81449 | 0.3946 | -0.44537
2.623 | -0.75631 | 0.34128 | -0.44368
2.6629 | -0.69814 | 0.29043 | -0.42628
2.7028 | -0.63996 | 0.24237 | -0.40888
2.7427 | -0.58178 | 0.1974 | -0.39148
2.7826 | -0.5236 | 0.15581 | -0.37408
2.8224 | -0.46542 | 0.11786 | -0.39207
2.8623 | -0.40725 | 0.083794 | -0.42184
2.9022 | -0.34907 | 0.05382 | -0.45162
2.9421 | -0.29089 | 0.029224 | -0.48139
2.982 | -0.23271 | 0.022996 | -0.45714
3.0219 | -0.17453 | 0.018111 | -0.34286
3.0618 | -0.11636 | 0.014599 | -0.22857
3.1017 | -0.058178 | 0.012482 | -0.11429
3.14 | 0 | 0.011775 | 0

## Airfoil FFA-W3-270blend
name | FFA-W3-270blend
relative_thickness | 0.27
aerodynamic_center | 0.25
x | y
1 | 0.00652
0.99185 | 0.00831
0.98371 | 0.0101
0.97556 | 0.01188
0.96742 | 0.01366
0.95928 | 0.01544
0.95114 | 0.01721
0.94301 | 0.01898
0.93488 | 0.02076
0.92675 | 0.02255
0.91863 | 0.02435
0.91052 | 0.02617
0.90241 | 0.02799
0.8943 | 0.02982
0.8862 | 0.03166
0.8781 | 0.0335
0.87001 | 0.03535
0.86192 | 0.03721
0.85384 | 0.03907
0.84576 | 0.04094
0.83768 | 0.04281
0.8296 | 0.04468
0.82153 | 0.04655
0.81346 | 0.04843
0.80539 | 0.05031
0.79732 | 0.05219
0.78926 | 0.05407
0.7812 | 0.05594
0.77314 | 0.05782
0.76508 | 0.05969
0.75702 | 0.06157
0.74897 | 0.06343
0.74091 | 0.0653
0.73285 | 0.06716
0.7248 | 0.06901
0.71675 | 0.07086
0.70869 | 0.0727
0.70064 | 0.07453
0.69258 | 0.07636
0.68452 | 0.07817
0.67647 | 0.07997
0.66841 | 0.08176
0.66035 | 0.08355
0.65229 | 0.08531
0.64422 | 0.08707
0.63616 | 0.08881
0.62809 | 0.09054
0.62002 | 0.09225
0.61195 | 0.09395
0.60387 | 0.09562
0.5958 | 0.09729
0.58772 | 0.09893
0.57963 | 0.10055
0.57154 | 0.10215
0.56345 | 0.10373
0.55536 | 0.10529
0.54726 | 0.10683
0.53916 | 0.10834
0.53105 | 0.10983
0.52294 | 0.11129
0.51482 | 0.11272
0.5067 | 0.11413
0.49858 | 0.11551
0.49045 | 0.11686
0.48231 | 0.11817
0.47417 | 0.11946
0.46603 | 0.1207
0.45787 | 0.12191
0.44972 | 0.12307
0.44155 | 0.1242
0.43338 | 0.12529
0.42521 | 0.12633
0.41702 | 0.12733
0.40884 | 0.12828
0.40064 | 0.12918
0.39244 | 0.13003
0.38424 | 0.13083
0.37602 | 0.13157
0.36781 | 0.13226
0.35958 | 0.13288
0.35135 | 0.13345
0.34312 | 0.13395
0.33488 | 0.13438
0.32664 | 0.13474
0.31839 | 0.13502
0.31014 | 0.13523
0.30188 | 0.13537
0.29363 | 0.13541
0.28537 | 0.13537
0.27711 | 0.13524
0.26886 | 0.13501
0.2606 | 0.13469
0.25235 | 0.13426
0.24411 | 0.13373
0.23587 | 0.13308
0.22763 | 0.13233
0.21941 | 0.13146
0.2112 | 0.13048
0.20301 | 0.12936
0.19483 | 0.12811
0.18668 | 0.12672
0.17855 | 0.12518
0.17045 | 0.1235
0.16238 | 0.12167
0.15434 | 0.11969
0.14635 | 0.11754
0.1384 | 0.11522
0.1305 | 0.11274
0.12265 | 0.11008
0.11487 | 0.10724
0.10716 | 0.10422
0.09952 | 0.10101
0.09197 | 0.09759
0.08451 | 0.09398
0.07715 | 0.09014
0.06991 | 0.08609
0.0628 | 0.0818
0.05584 | 0.07727
0.04905 | 0.07247
0.04245 | 0.06739
0.03607 | 0.06196
0.02994 | 0.05624
0.02413 | 0.05049
0.01869 | 0.04439
0.0137 | 0.03792
0.00923 | 0.03107
0.0054 | 0.02383
0.00249 | 0.01614
0.00064 | 0.00809
0 | -0.00019
0.00089 | -0.00845
0.00355 | -0.01641
0.00749 | -0.02407
0.01224 | -0.03122
0.01762 | -0.03781
0.0234 | -0.04403
0.02952 | -0.0499
0.03592 | -0.05547
0.04253 | -0.06076
0.04932 | -0.06581
0.05615 | -0.07063
0.06309 | -0.07523
0.07018 | -0.07962
0.0774 | -0.08382
0.08474 | -0.08782
0.09218 | -0.09164
0.09973 | -0.09527
0.10736 | -0.09873
0.11507 | -0.10201
0.12286 | -0.10512
0.13073 | -0.10805
0.13866 | -0.11082
0.14664 | -0.11341
0.15469 | -0.11584
0.16279 | -0.11811
0.17093 | -0.12022
0.17911 | -0.12218
0.18733 | -0.12397
0.19559 | -0.12562
0.20387 | -0.12711
0.21219 | -0.12846
0.22053 | -0.12966
0.22889 | -0.13073
0.23726 | -0.13166
0.24566 | -0.13245
0.25406 | -0.13312
0.26248 | -0.13365
0.2709 | -0.13406
0.27933 | -0.13435
0.28777 | -0.13451
0.2962 | -0.13455
0.30464 | -0.13447
0.31308 | -0.13428
0.32151 | -0.13397
0.32994 | -0.13354
0.33836 | -0.13301
0.34678 | -0.13236
0.35518 | -0.13161
0.36358 | -0.13075
0.37196 | -0.12978
0.38033 | -0.12871
0.38869 | -0.12753
0.39703 | -0.12626
0.40536 | -0.12489
0.41366 | -0.12341
0.42195 | -0.12185
0.43023 | -0.1202
0.43848 | -0.11845
0.44671 | -0.11662
0.45493 | -0.1147
0.46312 | -0.1127
0.47129 | -0.11061
0.47944 | -0.10845
0.48757 | -0.10621
0.49567 | -0.1039
0.50376 | -0.10152
0.51182 | -0.09907
0.51986 | -0.09656
0.52788 | -0.09399
0.53589 | -0.09137
0.54387 | -0.0887
0.55184 | -0.08599
0.55979 | -0.08323
0.56773 | -0.08044
0.57566 | -0.07761
0.58358 | -0.07476
0.59149 | -0.07188
0.59939 | -0.06898
0.60729 | -0.06607
0.61518 | -0.06315
0.62308 | -0.06024
0.63098 | -0.05732
0.63888 | -0.05441
0.64679 | -0.05152
0.65471 | -0.04864
0.66263 | -0.04579
0.67057 | -0.04297
0.67853 | -0.04019
0.68649 | -0.03745
0.69448 | -0.03476
0.70248 | -0.03213
0.7105 | -0.02955
0.71854 | -0.02704
0.7266 | -0.02459
0.73468 | -0.02222
0.74278 | -0.01993
0.75091 | -0.01771
0.75905 | -0.01559
0.76722 | -0.01356
0.77541 | -0.01163
0.78362 | -0.00982
0.79186 | -0.00814
0.80012 | -0.00656
0.80839 | -0.00511
0.81669 | -0.00377
0.82499 | -0.00254
0.83332 | -0.00143
0.84165 | -0.00044
0.85 | 0.00045
0.85835 | 0.00121
0.86671 | 0.00185
0.87508 | 0.00237
0.88346 | 0.00275
0.89184 | 0.003
0.90022 | 0.0031
0.90859 | 0.00305
0.91697 | 0.00287
0.92533 | 0.00254
0.93369 | 0.00207
0.94203 | 0.00147
0.95037 | 0.00074
0.95868 | -0.00012
0.96698 | -0.00112
0.97526 | -0.00224
0.98352 | -0.00347
0.99177 | -0.00479
1 | -0.00613
Reynolds | 10000000
alpha [rad] | c_l | c_d | c_m
-3.14 | 0 | 0.015451 | 0
-3.1017 | 0.062129 | 0.016108 | 0.091429
-3.0618 | 0.12426 | 0.018073 | 0.18286
-3.0219 | 0.18639 | 0.021333 | 0.27429
-2.982 | 0.24852 | 0.025868 | 0.36571
-2.9421 | 0.31064 | 0.032888 | 0.39874
-2.9022 | 0.37277 | 0.056807 | 0.39672
-2.8623 | 0.4349 | 0.084714 | 0.3947
-2.8224 | 0.49703 | 0.11643 | 0.39268
-2.7826 | 0.55916 | 0.15176 | 0.39544
-2.7427 | 0.62129 | 0.19048 | 0.41254
-2.7028 | 0.68342 | 0.23234 | 0.42964
-2.6629 | 0.74555 | 0.27708 | 0.44674
-2.623 | 0.80768 | 0.32441 | 0.46384
-2.5831 | 0.86981 | 0.37404 | 0.46186
-2.5108 | 0.8166 | 0.46882 | 0.45335
-2.4385 | 0.76812 | 0.56814 | 0.44523
-2.3662 | 0.7204 | 0.66995 | 0.44237
-2.2939 | 0.67095 | 0.77214 | 0.43951
-2.2216 | 0.61828 | 0.87258 | 0.44072
-2.1492 | 0.56158 | 0.96921 | 0.44407
-2.0769 | 0.50057 | 1.06 | 0.44739
-2.0046 | 0.4354 | 1.1432 | 0.45063
-1.9323 | 0.36655 | 1.2169 | 0.45387
-1.86 | 0.29475 | 1.2797 | 0.45377
-1.7877 | 0.22098 | 1.3303 | 0.45298
-1.7154 | 0.14639 | 1.3677 | 0.44973
-1.6431 | 0.072269 | 1.3911 | 0.44302
-1.5708 | 5.5511e-17 | 1.4 | 0.4363
-1.4985 | -0.072269 | 1.3911 | 0.4218
-1.4262 | -0.14639 | 1.3677 | 0.4073
-1.3539 | -0.22098 | 1.3303 | 0.3902
-1.2816 | -0.29475 | 1.2797 | 0.37125
-1.2093 | -0.36655 | 1.2169 | 0.3519
-1.137 | -0.4354 | 1.1432 | 0.33068
-1.0647 | -0.50057 | 1.06 | 0.30945
-0.99234 | -0.56158 | 0.96921 | 0.28815
-0.92004 | -0.61828 | 0.87258 | 0.26684
-0.84773 | -0.67095 | 0.77214 | 0.24576
-0.77542 | -0.7204 | 0.66995 | 0.22512
-0.70312 | -0.76812 | 0.56814 | 0.20447
-0.63081 | -0.8166 | 0.46882 | 0.13957
-0.55851 | -0.86981 | 0.37404 | 0.071382
-0.48869 | -1.0984 | 0.2188 | 0.043998
-0.41888 | -1.0834 | 0.15982 | 0.02166
-0.34907 | -1.0699 | 0.10744 | 0.0042194
-0.31416 | -1.0545 | 0.086904 | -0.00035185
-0.27925 | -1.0343 | 0.068443 | -0.0033372
-0.24435 | -1.0836 | 0.047334 | -0.0028317
-0.20944 | -1.0949 | 0.030849 | -0.0055562
-0.17453 | -0.92665 | 0.019843 | -0.029517
-0.13963 | -0.69676 | 0.014394 | -0.048218
-0.10472 | -0.43628 | 0.011549 | -0.064832
-0.069813 | -0.16252 | 0.010264 | -0.079187
-0.034907 | 0.10709 | 0.0097551 | -0.090407
-0.017453 | 0.23993 | 0.0096708 | -0.095173
0 | 0.37158 | 0.0096775 | -0.099533
0.017453 | 0.5021 | 0.0097641 | -0.10355
0.034907 | 0.63139 | 0.0099289 | -0.10725
0.05236 | 0.75951 | 0.010161 | -0.11068
0.069813 | 0.88638 | 0.010454 | -0.11385
0.087266 | 1.0117 | 0.010823 | -0.11673
0.10472 | 1.1343 | 0.011399 | -0.11923
0.12217 | 1.2554 | 0.011979 | -0.12145
0.13963 | 1.3738 | 0.012669 | -0.12328
0.15708 | 1.4884 | 0.01353 | -0.1246
0.17453 | 1.5978 | 0.014604 | -0.12526
0.19199 | 1.7001 | 0.015967 | -0.12505
0.20944 | 1.7919 | 0.017767 | -0.1237
0.22689 | 1.8678 | 0.02035 | -0.12093
0.24435 | 1.9269 | 0.02385 | -0.11725
0.2618 | 1.909 | 0.032357 | -0.10931
0.27925 | 1.8855 | 0.042586 | -0.10525
0.31416 | 1.7211 | 0.076715 | -0.10292
0.34907 | 1.5474 | 0.11914 | -0.11017
0.41888 | 1.3718 | 0.20189 | -0.13431
0.48869 | 1.3361 | 0.27981 | -0.15777
0.55851 | 1.2426 | 0.37404 | -0.18432
0.63081 | 1.1666 | 0.46882 | -0.21002
0.70312 | 1.0973 | 0.56814 | -0.23531
0.77542 | 1.0291 | 0.66995 | -0.25508
0.84773 | 0.9585 | 0.77214 | -0.27485
0.92004 | 0.88325 | 0.87258 | -0.29346
0.99234 | 0.80225 | 0.96921 | -0.31145
1.0647 | 0.7151 | 1.06 | -0.32925
1.137 | 0.622 | 1.1432 | -0.34641
1.2093 | 0.52364 | 1.2169 | -0.36357
1.2816 | 0.42107 | 1.2797 | -0.37949
1.3539 | 0.31569 | 1.3303 | -0.39517
1.4262 | 0.20913 | 1.3677 | -0.40983
1.4985 | 0.10324 | 1.3911 | -0.42306
1.5708 | 8.3267e-17 | 1.4 | -0.4363
1.6431 | -0.072269 | 1.3911 | -0.44302
1.7154 | -0.14639 | 1.3677 | -0.44973
1.7877 | -0.22098 | 1.3303 | -0.45298
1.86 | -0.29475 | 1.2797 | -0.45377
1.9323 | -0.36655 | 1.2169 | -0.45387
2.0046 | -0.4354 | 1.1432 | -0.45063
2.0769 | -0.50057 | 1.06 | -0.44739
2.1492 | -0.56158 | 0.96921 | -0.44407
2.2216 | -0.61828 | 0.87258 | -0.44072
2.2939 | -0.67095 | 0.77214 | -0.43951
2.3662 | -0.7204 | 0.66995 | -0.44237
2.4385 | -0.76812 | 0.56814 | -0.44523
2.5108 | -0.8166 | 0.46882 | -0.45335
2.5831 | -0.86981 | 0.37404 | -0.46186
2.623 | -0.80768 | 0.32441 | -0.46384
2.6629 | -0.74555 | 0.27708 | -0.44674
2.7028 | -0.68342 | 0.23234 | -0.42964
2.7427 | -0.62129 | 0.19048 | -0.41254
2.7826 | -0.55916 | 0.15176 | -0.39544
2.8224 | -0.49703 | 0.11643 | -0.40982
2.8623 | -0.4349 | 0.084714 | -0.4347
2.9022 | -0.37277 | 0.056807 | -0.45958
2.9421 | -0.31064 | 0.032888 | -0.48445
2.982 | -0.24852 | 0.025868 | -0.45714
3.0219 | -0.18639 | 0.021333 | -0.34286
3.0618 | -0.12426 | 0.018073 | -0.22857
3.1017 | -0.062129 | 0.016108 | -0.11429
3.14 | 0 | 0.015451 | 0

## Airfoil FFA-W3-301
name | FFA-W3-301
relative_thickness | 0.301
aerodynamic_center | 0.25
x | y
1 | 0.0091
0.99944 | 0.0092
0.99812 | 0.0095
0.99569 | 0.010191
0.9923 | 0.010987
0.98803 | 0.011993
0.98282 | 0.01322
0.97666 | 0.014669
0.96964 | 0.016325
0.96174 | 0.018189
0.95297 | 0.020262
0.94339 | 0.022529
0.93301 | 0.024989
0.92185 | 0.027656
0.90995 | 0.030536
0.89736 | 0.033613
0.88409 | 0.036882
0.87016 | 0.040328
0.85565 | 0.043942
0.84058 | 0.047719
0.82497 | 0.051634
0.80889 | 0.055681
0.79236 | 0.059826
0.77542 | 0.064066
0.75813 | 0.068384
0.7405 | 0.072757
0.72259 | 0.077169
0.70445 | 0.081593
0.68609 | 0.086
0.66757 | 0.090393
0.64893 | 0.094736
0.63019 | 0.099018
0.6114 | 0.10323
0.5926 | 0.10734
0.57381 | 0.11135
0.55508 | 0.11524
0.53642 | 0.11897
0.51788 | 0.12256
0.49948 | 0.126
0.48125 | 0.12923
0.46322 | 0.13226
0.44541 | 0.13506
0.42784 | 0.13763
0.41054 | 0.13995
0.39353 | 0.14203
0.37681 | 0.14383
0.36042 | 0.14537
0.34436 | 0.14664
0.32866 | 0.14763
0.31332 | 0.14835
0.29835 | 0.14878
0.28377 | 0.14892
0.26957 | 0.14878
0.25577 | 0.14835
0.24238 | 0.14764
0.2294 | 0.14666
0.21682 | 0.14541
0.20466 | 0.14389
0.19291 | 0.14212
0.18157 | 0.1401
0.17066 | 0.13784
0.16015 | 0.13536
0.15006 | 0.13268
0.14035 | 0.12981
0.13107 | 0.12676
0.12216 | 0.12357
0.11366 | 0.12023
0.10554 | 0.11677
0.097791 | 0.11319
0.090429 | 0.10953
0.083416 | 0.10579
0.076774 | 0.10198
0.070469 | 0.098121
0.0645 | 0.094223
0.058882 | 0.090316
0.053568 | 0.086375
0.048576 | 0.082428
0.043898 | 0.078495
0.039495 | 0.074555
0.035395 | 0.070655
0.031576 | 0.066783
0.028006 | 0.062927
0.024716 | 0.059123
0.021681 | 0.055364
0.018863 | 0.051615
0.016295 | 0.047935
0.013966 | 0.044343
0.011818 | 0.040736
0.0098836 | 0.03723
0.0081837 | 0.033847
0.0066313 | 0.030417
0.0052485 | 0.027079
0.0040827 | 0.023859
0.00309 | 0.020692
0.002191 | 0.017626
0.0014597 | 0.014402
0.00096333 | 0.011485
0.00059878 | 0.0081594
0.00028988 | 0.0039343
7.804e-05 | 0.0009904
0 | 0
7.807e-05 | -0.00098225
0.00029009 | -0.0038427
0.00059937 | -0.0079089
0.00096448 | -0.011194
0.0014626 | -0.013959
0.0021966 | -0.017027
0.0030988 | -0.019863
0.0040952 | -0.022777
0.0052677 | -0.025854
0.0066584 | -0.029027
0.0082194 | -0.032254
0.0099309 | -0.035475
0.01188 | -0.038798
0.014045 | -0.042224
0.016392 | -0.045662
0.018985 | -0.049187
0.021829 | -0.052812
0.024893 | -0.056457
0.02822 | -0.060182
0.031829 | -0.063977
0.03569 | -0.067814
0.039842 | -0.071712
0.0443 | -0.075671
0.049038 | -0.079648
0.0541 | -0.083659
0.059487 | -0.087691
0.065188 | -0.091728
0.071248 | -0.095775
0.077646 | -0.0998
0.084397 | -0.1038
0.091523 | -0.10777
0.099007 | -0.11167
0.10689 | -0.11551
0.11515 | -0.11925
0.12381 | -0.12288
0.13287 | -0.1264
0.14233 | -0.12976
0.15221 | -0.13296
0.1625 | -0.13598
0.17321 | -0.1388
0.18434 | -0.14139
0.1959 | -0.14375
0.20788 | -0.14585
0.22029 | -0.14768
0.23312 | -0.14922
0.24637 | -0.15044
0.26004 | -0.15134
0.27412 | -0.1519
0.28861 | -0.15208
0.3035 | -0.15188
0.31877 | -0.15128
0.33443 | -0.15027
0.35046 | -0.14881
0.36684 | -0.1469
0.38356 | -0.14451
0.40061 | -0.14165
0.41796 | -0.13829
0.43559 | -0.13444
0.45349 | -0.1301
0.47163 | -0.12526
0.48999 | -0.11993
0.50854 | -0.11414
0.52725 | -0.10792
0.54609 | -0.10132
0.56503 | -0.09438
0.58405 | -0.08718
0.60309 | -0.079795
0.62214 | -0.072304
0.64115 | -0.064818
0.66008 | -0.057433
0.67891 | -0.050235
0.69757 | -0.043331
0.71604 | -0.036803
0.73429 | -0.03072
0.75225 | -0.025123
0.7699 | -0.020046
0.78719 | -0.01556
0.80407 | -0.0117
0.82051 | -0.0084086
0.83647 | -0.0056702
0.85189 | -0.0034675
0.86675 | -0.0017734
0.88101 | -0.00057044
0.89461 | 0.00016442
0.90752 | 0.00045227
0.91973 | 0.00040686
0.93118 | 4.808e-05
0.94183 | -0.00057005
0.95168 | -0.0014277
0.96067 | -0.0024128
0.96879 | -0.00347
0.97601 | -0.0045494
0.98233 | -0.0056022
0.98769 | -0.0065754
0.99209 | -0.0074312
0.99557 | -0.008146
0.99806 | -0.008676
0.99943 | -0.0089741
1 | -0.0091
Reynolds | 10000000
alpha [rad] | c_l | c_d | c_m
-3.14 | 0 | 0.02454 | 0
-3.1017 | 0.065082 | 0.025141 | 0.091429
-3.0618 | 0.13016 | 0.026941 | 0.18286
-3.0219 | 0.19525 | 0.029929 | 0.27429
-2.982 | 0.26033 | 0.034084 | 0.36571
-2.9421 | 0.32541 | 0.039379 | 0.40085
-2.9022 | 0.39049 | 0.059103 | 0.4022
-2.8623 | 0.45557 | 0.084949 | 0.40356
-2.8224 | 0.52066 | 0.11433 | 0.40492
-2.7826 | 0.58574 | 0.14704 | 0.4101
-2.7427 | 0.65082 | 0.1829 | 0.42678
-2.7028 | 0.7159 | 0.22166 | 0.44345
-2.6629 | 0.78098 | 0.26309 | 0.46013
-2.623 | 0.84607 | 0.30692 | 0.4768
-2.5831 | 0.91115 | 0.35287 | 0.47162
-2.5108 | 0.84257 | 0.44061 | 0.45656
-2.4385 | 0.78187 | 0.53255 | 0.44202
-2.3662 | 0.72448 | 0.62677 | 0.43452
-2.2939 | 0.66755 | 0.72131 | 0.42701
-2.2216 | 0.60928 | 0.81421 | 0.42483
-2.1492 | 0.54868 | 0.90355 | 0.42544
-2.0769 | 0.4853 | 0.98748 | 0.42634
-2.0046 | 0.41915 | 1.0642 | 0.42813
-1.9323 | 0.35056 | 1.1323 | 0.42992
-1.86 | 0.28017 | 1.1902 | 0.42916
-1.7877 | 0.20881 | 1.2367 | 0.42788
-1.7154 | 0.13754 | 1.2709 | 0.42444
-1.6431 | 0.067506 | 1.2922 | 0.41794
-1.5708 | 5.5511e-17 | 1.3 | 0.41144
-1.4985 | -0.067506 | 1.2922 | 0.39804
-1.4262 | -0.13754 | 1.2709 | 0.38464
-1.3539 | -0.20881 | 1.2367 | 0.36892
-1.2816 | -0.28017 | 1.1902 | 0.35157
-1.2093 | -0.35056 | 1.1323 | 0.33391
-1.137 | -0.41915 | 1.0642 | 0.31474
-1.0647 | -0.4853 | 0.98748 | 0.29557
-0.99234 | -0.54868 | 0.90355 | 0.27653
-0.92004 | -0.60928 | 0.81421 | 0.25754
-0.84773 | -0.66755 | 0.72131 | 0.23873
-0.77542 | -0.72448 | 0.62677 | 0.22027
-0.70312 | -0.78187 | 0.53255 | 0.20181
-0.63081 | -0.84257 | 0.44061 | 0.13644
-0.55851 | -0.91115 | 0.35287 | 0.067597
-0.48869 | -1.1035 | 0.21721 | 0.042306
-0.41888 | -1.1074 | 0.15629 | 0.020255
-0.34907 | -1.1182 | 0.10335 | 0.0040659
-0.31416 | -1.1233 | 0.081804 | 0.0001727
-0.27925 | -1.1187 | 0.063307 | -0.0016692
-0.24435 | -1.1162 | 0.047183 | -0.0011956
-0.20944 | -1.0959 | 0.032802 | -0.004634
-0.17453 | -0.91767 | 0.023515 | -0.024936
-0.13963 | -0.69311 | 0.017929 | -0.043039
-0.10472 | -0.45396 | 0.014306 | -0.058675
-0.069813 | -0.17779 | 0.012423 | -0.076012
-0.034907 | 0.1048 | 0.011595 | -0.091212
-0.017453 | 0.24383 | 0.01143 | -0.097633
0 | 0.38111 | 0.011381 | -0.10341
0.017453 | 0.5166 | 0.011432 | -0.10861
0.034907 | 0.65044 | 0.011564 | -0.11333
0.05236 | 0.78267 | 0.011767 | -0.11762
0.069813 | 0.91326 | 0.012042 | -0.12154
0.087266 | 1.0421 | 0.012393 | -0.1251
0.10472 | 1.1687 | 0.012834 | -0.12828
0.12217 | 1.293 | 0.013379 | -0.13104
0.13963 | 1.4139 | 0.014059 | -0.13332
0.15708 | 1.5309 | 0.014882 | -0.13503
0.17453 | 1.6421 | 0.015919 | -0.13599
0.19199 | 1.7457 | 0.017257 | -0.13605
0.20944 | 1.8389 | 0.019079 | -0.13514
0.22689 | 1.9176 | 0.021687 | -0.13322
0.24435 | 1.9741 | 0.02572 | -0.1302
0.2618 | 1.9992 | 0.03222 | -0.12641
0.27925 | 1.9938 | 0.041569 | -0.12265
0.31416 | 1.9172 | 0.067308 | -0.11675
0.34907 | 1.7368 | 0.10526 | -0.11652
0.41888 | 1.4732 | 0.19229 | -0.1379
0.48869 | 1.3602 | 0.27449 | -0.16242
0.55851 | 1.3016 | 0.35287 | -0.18463
0.63081 | 1.2037 | 0.44061 | -0.20894
0.70312 | 1.117 | 0.53255 | -0.23276
0.77542 | 1.035 | 0.62677 | -0.25011
0.84773 | 0.95364 | 0.72131 | -0.26746
0.92004 | 0.8704 | 0.81421 | -0.28365
0.99234 | 0.78383 | 0.90355 | -0.29923
1.0647 | 0.69329 | 0.98748 | -0.31472
1.137 | 0.59878 | 1.0642 | -0.32988
1.2093 | 0.5008 | 1.1323 | -0.34505
1.2816 | 0.40024 | 1.1902 | -0.35942
1.3539 | 0.29831 | 1.2367 | -0.37363
1.4262 | 0.19648 | 1.2709 | -0.38702
1.4985 | 0.096437 | 1.2922 | -0.39923
1.5708 | 8.3267e-17 | 1.3 | -0.41144
1.6431 | -0.067506 | 1.2922 | -0.41794
1.7154 | -0.13754 | 1.2709 | -0.42444
1.7877 | -0.20881 | 1.2367 | -0.42788
1.86 | -0.28017 | 1.1902 | -0.42916
1.9323 | -0.35056 | 1.1323 | -0.42992
2.0046 | -0.41915 | 1.0642 | -0.42813
2.0769 | -0.4853 | 0.98748 | -0.42634
2.1492 | -0.54868 | 0.90355 | -0.42544
2.2216 | -0.60928 | 0.81421 | -0.42483
2.2939 | -0.66755 | 0.72131 | -0.42701
2.3662 | -0.72448 | 0.62677 | -0.43452
2.4385 | -0.78187 | 0.53255 | -0.44202
2.5108 | -0.84257 | 0.44061 | -0.45656
2.5831 | -0.91115 | 0.35287 | -0.47162
2.623 | -0.84607 | 0.30692 | -0.4768
2.6629 | -0.78098 | 0.26309 | -0.46013
2.7028 | -0.7159 | 0.22166 | -0.44345
2.7427 | -0.65082 | 0.1829 | -0.42678
2.7826 | -0.58574 | 0.14704 | -0.4101
2.8224 | -0.52066 | 0.11433 | -0.42206
2.8623 | -0.45557 | 0.084949 | -0.44356
2.9022 | -0.39049 | 0.059103 | -0.46506
2.9421 | -0.32541 | 0.039379 | -0.48656
2.982 | -0.26033 | 0.034084 | -0.45714
3.0219 | -0.19525 | 0.029929 | -0.34286
3.0618 | -0.13016 | 0.026941 | -0.22857
3.1017 | -0.065082 | 0.025141 | -0.11429
3.14 | 0 | 0.02454 | 0

## Airfoil FFA-W3-330blend
name | FFA-W3-330blend
relative_thickness | 0.33
aerodynamic_center | 0.25
x | y
1 | 0.01245
0.9917 | 0.0146
0.98339 | 0.01675
0.97509 | 0.01888
0.96678 | 0.021
0.95847 | 0.0231
0.95016 | 0.0252
0.94186 | 0.0273
0.93356 | 0.0294
0.92526 | 0.03151
0.91697 | 0.03364
0.90869 | 0.03578
0.90042 | 0.03793
0.89215 | 0.04009
0.88388 | 0.04226
0.87562 | 0.04443
0.86736 | 0.0466
0.85911 | 0.04878
0.85086 | 0.05097
0.84261 | 0.05315
0.83437 | 0.05535
0.82613 | 0.05754
0.81789 | 0.05973
0.80966 | 0.06193
0.80143 | 0.06412
0.7932 | 0.0663
0.78497 | 0.06849
0.77674 | 0.07067
0.76852 | 0.07285
0.76029 | 0.07503
0.75207 | 0.0772
0.74385 | 0.07937
0.73562 | 0.08153
0.7274 | 0.08369
0.71918 | 0.08584
0.71096 | 0.08798
0.70273 | 0.09011
0.69451 | 0.09223
0.68629 | 0.09434
0.67806 | 0.09644
0.66983 | 0.09853
0.66161 | 0.10062
0.65338 | 0.10268
0.64514 | 0.10474
0.63691 | 0.10678
0.62867 | 0.10881
0.62044 | 0.11083
0.61219 | 0.11283
0.60395 | 0.11481
0.5957 | 0.11678
0.58745 | 0.11874
0.5792 | 0.12067
0.57094 | 0.12259
0.56268 | 0.12449
0.55441 | 0.12636
0.54614 | 0.12822
0.53787 | 0.13005
0.52959 | 0.13187
0.5213 | 0.13365
0.51301 | 0.13542
0.50471 | 0.13715
0.49641 | 0.13886
0.48813 | 0.14053
0.47986 | 0.14218
0.47159 | 0.14378
0.4633 | 0.14536
0.45501 | 0.14689
0.44671 | 0.14838
0.4384 | 0.14984
0.43008 | 0.15124
0.42176 | 0.1526
0.41342 | 0.15392
0.40507 | 0.15518
0.39672 | 0.15639
0.38835 | 0.15755
0.37998 | 0.15865
0.37159 | 0.15969
0.3632 | 0.16067
0.35479 | 0.16158
0.34638 | 0.16242
0.33796 | 0.16319
0.32953 | 0.16389
0.32109 | 0.16451
0.31264 | 0.16504
0.30418 | 0.16549
0.29572 | 0.16586
0.28725 | 0.16613
0.27878 | 0.1663
0.2703 | 0.16636
0.26182 | 0.16632
0.25334 | 0.16615
0.24486 | 0.16587
0.23638 | 0.16546
0.2279 | 0.16491
0.21943 | 0.16423
0.21097 | 0.1634
0.20253 | 0.1624
0.1941 | 0.16125
0.1857 | 0.15991
0.17733 | 0.15839
0.16898 | 0.15668
0.16068 | 0.15478
0.15243 | 0.15266
0.14423 | 0.15033
0.1361 | 0.14779
0.12803 | 0.14502
0.12004 | 0.14203
0.11215 | 0.1388
0.10436 | 0.13531
0.09669 | 0.13157
0.08915 | 0.12757
0.08176 | 0.12331
0.07453 | 0.11877
0.06748 | 0.11395
0.06064 | 0.10886
0.05402 | 0.10348
0.04763 | 0.09783
0.04151 | 0.09189
0.03567 | 0.08568
0.03015 | 0.07919
0.02498 | 0.07242
0.02018 | 0.06539
0.01577 | 0.0581
0.01178 | 0.05056
0.0083 | 0.04277
0.00551 | 0.03473
0.0034 | 0.02648
0.00177 | 0.01806
0.00052 | 0.00955
0 | 0.00098
0.00048 | -0.00761
0.00174 | -0.01613
0.00344 | -0.02443
0.00581 | -0.03254
0.00892 | -0.04061
0.01269 | -0.0484
0.01696 | -0.05589
0.02165 | -0.0631
0.02674 | -0.07004
0.03223 | -0.07669
0.03808 | -0.08304
0.04424 | -0.0891
0.05068 | -0.09487
0.05737 | -0.10036
0.06428 | -0.10559
0.07139 | -0.11054
0.07869 | -0.11522
0.08616 | -0.11964
0.09378 | -0.1238
0.10153 | -0.12771
0.1094 | -0.13138
0.11738 | -0.13483
0.12545 | -0.13805
0.13361 | -0.14107
0.14184 | -0.14388
0.15013 | -0.14648
0.15849 | -0.14889
0.16691 | -0.15111
0.17537 | -0.15313
0.18388 | -0.15498
0.19242 | -0.15666
0.20099 | -0.15816
0.2096 | -0.1595
0.21822 | -0.16068
0.22687 | -0.16169
0.23554 | -0.16255
0.24423 | -0.16325
0.25292 | -0.16381
0.26162 | -0.16421
0.27033 | -0.16447
0.27905 | -0.16458
0.28776 | -0.16456
0.29648 | -0.1644
0.30519 | -0.1641
0.31389 | -0.16368
0.32259 | -0.16312
0.33128 | -0.16244
0.33996 | -0.16164
0.34863 | -0.16071
0.35728 | -0.15967
0.36592 | -0.15851
0.37455 | -0.15723
0.38315 | -0.15585
0.39174 | -0.15435
0.40031 | -0.15274
0.40885 | -0.15103
0.41738 | -0.14921
0.42588 | -0.14729
0.43435 | -0.14527
0.44281 | -0.14316
0.45123 | -0.14094
0.45963 | -0.13864
0.46801 | -0.13625
0.47636 | -0.13378
0.48469 | -0.13123
0.493 | -0.12861
0.50128 | -0.12592
0.50954 | -0.12316
0.51777 | -0.12034
0.52599 | -0.11746
0.53418 | -0.11452
0.54235 | -0.11153
0.5505 | -0.10849
0.55863 | -0.1054
0.56675 | -0.10226
0.57484 | -0.09909
0.58293 | -0.09589
0.591 | -0.09265
0.59905 | -0.08939
0.6071 | -0.08611
0.61517 | -0.08281
0.62324 | -0.0795
0.63131 | -0.07618
0.63937 | -0.07286
0.64743 | -0.06955
0.65549 | -0.06624
0.66356 | -0.06295
0.67163 | -0.05968
0.67971 | -0.05644
0.6878 | -0.05323
0.6959 | -0.05005
0.70402 | -0.04693
0.71216 | -0.04386
0.72031 | -0.04085
0.72849 | -0.0379
0.73669 | -0.03502
0.74491 | -0.03221
0.75315 | -0.02949
0.76143 | -0.02685
0.76973 | -0.02431
0.77805 | -0.02187
0.78641 | -0.01954
0.7948 | -0.01733
0.80321 | -0.01523
0.81165 | -0.01325
0.82012 | -0.01138
0.82861 | -0.00965
0.83712 | -0.00805
0.84566 | -0.00658
0.85422 | -0.00526
0.8628 | -0.0041
0.87141 | -0.0031
0.88003 | -0.00227
0.88866 | -0.00161
0.89733 | -0.00114
0.90601 | -0.00084
0.91468 | -0.00073
0.92334 | -0.00081
0.93199 | -0.00107
0.94063 | -0.00152
0.94925 | -0.00216
0.95784 | -0.00302
0.96639 | -0.00415
0.97489 | -0.00559
0.98332 | -0.00734
0.99168 | -0.00939
1 | -0.01163
Reynolds | 10000000
alpha [rad] | c_l | c_d | c_m
-3.14 | 0 | 0.031686 | 0
-3.1017 | 0.069601 | 0.032281 | 0.091429
-3.0618 | 0.1392 | 0.034065 | 0.18286
-3.0219 | 0.2088 | 0.037024 | 0.27429
-2.982 | 0.27841 | 0.041139 | 0.36571
-2.9421 | 0.34801 | 0.046383 | 0.40308
-2.9022 | 0.41761 | 0.05732 | 0.40801
-2.8623 | 0.48721 | 0.083186 | 0.41294
-2.8224 | 0.55681 | 0.11258 | 0.41788
-2.7826 | 0.62641 | 0.14533 | 0.42586
-2.7427 | 0.69601 | 0.18121 | 0.44302
-2.7028 | 0.76562 | 0.22 | 0.46017
-2.6629 | 0.83522 | 0.26146 | 0.47732
-2.623 | 0.90482 | 0.30532 | 0.49447
-2.5831 | 0.97442 | 0.35131 | 0.48743
-2.5108 | 0.89412 | 0.43913 | 0.46839
-2.4385 | 0.82382 | 0.53115 | 0.44996
-2.3662 | 0.75845 | 0.62546 | 0.43985
-2.2939 | 0.69477 | 0.7201 | 0.42974
-2.2216 | 0.63079 | 0.8131 | 0.42589
-2.1492 | 0.56532 | 0.90255 | 0.42535
-2.0769 | 0.49783 | 0.98659 | 0.42528
-2.0046 | 0.42823 | 1.0635 | 0.42673
-1.9323 | 0.3568 | 1.1316 | 0.42817
-1.86 | 0.28412 | 1.1896 | 0.42745
-1.7877 | 0.21103 | 1.2363 | 0.42628
-1.7154 | 0.13851 | 1.2707 | 0.42303
-1.6431 | 0.06775 | 1.292 | 0.41683
-1.5708 | 5.5511e-17 | 1.3 | 0.41063
-1.4985 | -0.06775 | 1.292 | 0.39752
-1.4262 | -0.13851 | 1.2707 | 0.38441
-1.3539 | -0.21103 | 1.2363 | 0.36905
-1.2816 | -0.28412 | 1.1896 | 0.35212
-1.2093 | -0.3568 | 1.1316 | 0.33491
-1.137 | -0.42823 | 1.0635 | 0.31634
-1.0647 | -0.49783 | 0.98659 | 0.29777
-0.99234 | -0.56532 | 0.90255 | 0.27947
-0.92004 | -0.63079 | 0.8131 | 0.26125
-0.84773 | -0.69477 | 0.7201 | 0.24322
-0.77542 | -0.75845 | 0.62546 | 0.22556
-0.70312 | -0.82382 | 0.53115 | 0.20789
-0.63081 | -0.89412 | 0.43913 | 0.13731
-0.55851 | -0.97442 | 0.35131 | 0.062799
-0.48869 | -1.1631 | 0.20648 | 0.039049
-0.41888 | -1.1489 | 0.15001 | 0.01853
-0.34907 | -1.0945 | 0.106 | 0.0044075
-0.31416 | -1.058 | 0.087319 | -0.00060625
-0.27925 | -1.0228 | 0.07051 | -0.0034157
-0.24435 | -0.9981 | 0.054741 | -0.0040144
-0.20944 | -0.98515 | 0.040516 | -0.0027205
-0.17453 | -0.89583 | 0.02929 | -0.011979
-0.13963 | -0.67539 | 0.022067 | -0.034578
-0.10472 | -0.43247 | 0.017352 | -0.054656
-0.069813 | -0.15881 | 0.014727 | -0.074255
-0.034907 | 0.13456 | 0.013624 | -0.092697
-0.017453 | 0.28014 | 0.013391 | -0.10074
0 | 0.42386 | 0.013299 | -0.10802
0.017453 | 0.56519 | 0.013325 | -0.1145
0.034907 | 0.7041 | 0.01345 | -0.12028
0.05236 | 0.84071 | 0.013665 | -0.12546
0.069813 | 0.975 | 0.01397 | -0.13011
0.087266 | 1.1068 | 0.014369 | -0.13425
0.10472 | 1.236 | 0.014862 | -0.13793
0.12217 | 1.3622 | 0.015472 | -0.14108
0.13963 | 1.4842 | 0.016227 | -0.14363
0.15708 | 1.601 | 0.017176 | -0.14545
0.17453 | 1.7101 | 0.018408 | -0.14636
0.19199 | 1.8096 | 0.020096 | -0.14635
0.20944 | 1.8947 | 0.02258 | -0.14544
0.22689 | 1.957 | 0.026709 | -0.14378
0.24435 | 1.9858 | 0.033802 | -0.14185
0.2618 | 1.9926 | 0.043331 | -0.14004
0.27925 | 1.9962 | 0.053544 | -0.13823
0.31416 | 1.964 | 0.07706 | -0.13351
0.34907 | 1.8118 | 0.11169 | -0.13135
0.41888 | 1.5607 | 0.19103 | -0.1466
0.48869 | 1.468 | 0.27199 | -0.17242
0.55851 | 1.392 | 0.35131 | -0.19417
0.63081 | 1.2773 | 0.43913 | -0.21792
0.70312 | 1.1769 | 0.53115 | -0.24115
0.77542 | 1.0835 | 0.62546 | -0.25734
0.84773 | 0.99253 | 0.7201 | -0.27354
0.92004 | 0.90112 | 0.8131 | -0.28862
0.99234 | 0.8076 | 0.90255 | -0.30311
1.0647 | 0.71119 | 0.98659 | -0.31757
1.137 | 0.61175 | 1.0635 | -0.33194
1.2093 | 0.50971 | 1.1316 | -0.34631
1.2816 | 0.40589 | 1.1896 | -0.36014
1.3539 | 0.30146 | 1.2363 | -0.37385
1.4262 | 0.19788 | 1.2707 | -0.38681
1.4985 | 0.096786 | 1.292 | -0.39872
1.5708 | 8.3267e-17 | 1.3 | -0.41063
1.6431 | -0.06775 | 1.292 | -0.41683
1.7154 | -0.13851 | 1.2707 | -0.42303
1.7877 | -0.21103 | 1.2363 | -0.42628
1.86 | -0.28412 | 1.1896 | -0.42745
1.9323 | -0.3568 | 1.1316 | -0.42817
2.0046 | -0.42823 | 1.0635 | -0.42673
2.0769 | -0.49783 | 0.98659 | -0.42528
2.1492 | -0.56532 | 0.90255 | -0.42535
2.2216 | -0.63079 | 0.8131 | -0.42589
2.2939 | -0.69477 | 0.7201 | -0.42974
2.3662 | -0.75845 | 0.62546 | -0.43985
2.4385 | -0.82382 | 0.53115 | -0.44996
2.5108 | -0.89412 | 0.43913 | -0.46839
2.5831 | -0.97442 | 0.35131 | -0.48743
2.623 | -0.90482 | 0.30532 | -0.49447
2.6629 | -0.83522 | 0.26146 | -0.47732
2.7028 | -0.76562 | 0.22 | -0.46017
2.7427 | -0.69601 | 0.18121 | -0.44302
2.7826 | -0.62641 | 0.14533 | -0.42586
2.8224 | -0.55681 | 0.11258 | -0.43502
2.8623 | -0.48721 | 0.083186 | -0.45294
2.9022 | -0.41761 | 0.05732 | -0.47087
2.9421 | -0.34801 | 0.046383 | -0.4888
2.982 | -0.27841 | 0.041139 | -0.45714
3.0219 | -0.2088 | 0.037024 | -0.34286
3.0618 | -0.1392 | 0.034065 | -0.22857
3.1017 | -0.069601 | 0.032281 | -0.11429
3.14 | 0 | 0.031686 | 0

## Airfoil FFA-W3-360
name | FFA-W3-360
relative_thickness | 0.36
aerodynamic_center | 0.25
x | y
1 | 0.01298
0.99944 | 0.013259
0.99812 | 0.013537
0.99569 | 0.014255
0.9923 | 0.015254
0.98803 | 0.016511
0.98282 | 0.018037
0.97666 | 0.019828
0.96964 | 0.021864
0.96174 | 0.024141
0.95297 | 0.026657
0.94339 | 0.029394
0.93301 | 0.032321
0.92185 | 0.035461
0.90995 | 0.038828
0.89736 | 0.042419
0.88409 | 0.046219
0.87016 | 0.050211
0.85565 | 0.054375
0.84058 | 0.058712
0.82497 | 0.063204
0.80889 | 0.067832
0.79236 | 0.072584
0.77542 | 0.077445
0.75813 | 0.08239
0.7405 | 0.087405
0.72259 | 0.092487
0.70445 | 0.097591
0.68609 | 0.10272
0.66757 | 0.10785
0.64893 | 0.11295
0.63019 | 0.11803
0.6114 | 0.12305
0.5926 | 0.12799
0.57381 | 0.13283
0.55508 | 0.13755
0.53642 | 0.14213
0.51788 | 0.14656
0.49948 | 0.1508
0.48125 | 0.15483
0.46322 | 0.15865
0.44541 | 0.16221
0.42784 | 0.16553
0.41054 | 0.16856
0.39353 | 0.17132
0.37681 | 0.17376
0.36042 | 0.17591
0.34436 | 0.17774
0.32866 | 0.17926
0.31332 | 0.18046
0.29835 | 0.18133
0.28377 | 0.18188
0.26957 | 0.18211
0.25577 | 0.18204
0.24238 | 0.18164
0.2294 | 0.18094
0.21682 | 0.17993
0.20466 | 0.17862
0.19291 | 0.17702
0.18157 | 0.17511
0.17066 | 0.17293
0.16015 | 0.17049
0.15006 | 0.16779
0.14035 | 0.16485
0.13107 | 0.16169
0.12216 | 0.15833
0.11366 | 0.15479
0.10554 | 0.15108
0.097791 | 0.14721
0.090429 | 0.14319
0.083416 | 0.13901
0.076774 | 0.13472
0.070469 | 0.13032
0.0645 | 0.12582
0.058882 | 0.12122
0.053568 | 0.11653
0.048576 | 0.11179
0.043898 | 0.107
0.039495 | 0.10215
0.035395 | 0.097293
0.031576 | 0.092423
0.028006 | 0.087512
0.024716 | 0.082622
0.021681 | 0.077746
0.018863 | 0.072823
0.016295 | 0.06793
0.013966 | 0.063145
0.011818 | 0.058394
0.0098836 | 0.053712
0.0081837 | 0.049301
0.0066313 | 0.044623
0.0052485 | 0.039552
0.0040827 | 0.034234
0.00309 | 0.028127
0.002191 | 0.021599
0.0014597 | 0.01656
0.00096333 | 0.012525
0.00059878 | 0.0086197
0.00028988 | 0.0043303
7.804e-05 | 0.0011648
0 | 0
7.807e-05 | -0.0012214
0.00029009 | -0.0049302
0.00059937 | -0.010066
0.00096448 | -0.014042
0.0014626 | -0.018185
0.0021966 | -0.02326
0.0030988 | -0.028951
0.0040952 | -0.034027
0.0052677 | -0.038674
0.0066584 | -0.04323
0.0082194 | -0.047687
0.0099309 | -0.051948
0.01188 | -0.0564
0.014045 | -0.060956
0.016392 | -0.065501
0.018985 | -0.070153
0.021829 | -0.074836
0.024893 | -0.07944
0.02822 | -0.084032
0.031829 | -0.088619
0.03569 | -0.093153
0.039842 | -0.097677
0.0443 | -0.1022
0.049038 | -0.10668
0.0541 | -0.11114
0.059487 | -0.11555
0.065188 | -0.11989
0.071248 | -0.12417
0.077646 | -0.12835
0.084397 | -0.13245
0.091523 | -0.13644
0.099007 | -0.14033
0.10689 | -0.14411
0.11515 | -0.14776
0.12381 | -0.1513
0.13287 | -0.1547
0.14233 | -0.15793
0.15221 | -0.16099
0.1625 | -0.16386
0.17321 | -0.16653
0.18434 | -0.16899
0.1959 | -0.17121
0.20788 | -0.17318
0.22029 | -0.17489
0.23312 | -0.1763
0.24637 | -0.17738
0.26004 | -0.17813
0.27412 | -0.1785
0.28861 | -0.17852
0.3035 | -0.17811
0.31877 | -0.17729
0.33443 | -0.17604
0.35046 | -0.17434
0.36684 | -0.17216
0.38356 | -0.1695
0.40061 | -0.16633
0.41796 | -0.16264
0.43559 | -0.1584
0.45349 | -0.15362
0.47163 | -0.14833
0.48999 | -0.14257
0.50854 | -0.13636
0.52725 | -0.12974
0.54609 | -0.12273
0.56503 | -0.11537
0.58405 | -0.10772
0.60309 | -0.099844
0.62214 | -0.091786
0.64115 | -0.083648
0.66008 | -0.075518
0.67891 | -0.067495
0.69757 | -0.05968
0.71604 | -0.052192
0.73429 | -0.045098
0.75225 | -0.038499
0.7699 | -0.03246
0.78719 | -0.027003
0.80407 | -0.022133
0.82051 | -0.017863
0.83647 | -0.014198
0.85189 | -0.011163
0.86675 | -0.0087689
0.88101 | -0.0069716
0.89461 | -0.0057485
0.90752 | -0.0050322
0.91973 | -0.0047916
0.93118 | -0.004
0.94183 | -0.0037
0.95168 | -0.0034
0.96067 | -0.0031
0.96879 | -0.0028
0.97601 | -0.0025
0.98233 | -0.0022
0.98769 | -0.0019
0.99209 | -0.0016
0.99557 | -0.0013
0.99806 | -0.001
0.99943 | -0.0007
1 | -0.0007
Reynolds | 10000000
alpha [rad] | c_l | c_d | c_m
-3.14 | 0 | 0.037148 | 0
-3.1017 | 0.071781 | 0.037739 | 0.091429
-3.0618 | 0.14356 | 0.039509 | 0.18286
-3.0219 | 0.21534 | 0.042446 | 0.27429
-2.982 | 0.28713 | 0.046531 | 0.36571
-2.9421 | 0.35891 | 0.051737 | 0.40313
-2.9022 | 0.43069 | 0.060678 | 0.40814
-2.8623 | 0.50247 | 0.086508 | 0.41315
-2.8224 | 0.57425 | 0.11586 | 0.41816
-2.7826 | 0.64603 | 0.14856 | 0.42627
-2.7427 | 0.71781 | 0.18439 | 0.4437
-2.7028 | 0.7896 | 0.22313 | 0.46114
-2.6629 | 0.86138 | 0.26453 | 0.47857
-2.623 | 0.93316 | 0.30832 | 0.496
-2.5831 | 1.0049 | 0.35424 | 0.4883
-2.5108 | 0.91898 | 0.44192 | 0.46784
-2.4385 | 0.84406 | 0.53379 | 0.44803
-2.3662 | 0.77483 | 0.62793 | 0.43697
-2.2939 | 0.7079 | 0.72238 | 0.42591
-2.2216 | 0.64116 | 0.8152 | 0.4215
-2.1492 | 0.57335 | 0.90444 | 0.42058
-2.0769 | 0.50388 | 0.98826 | 0.42024
-2.0046 | 0.43261 | 1.0649 | 0.42168
-1.9323 | 0.35981 | 1.1328 | 0.42312
-1.86 | 0.28603 | 1.1906 | 0.42258
-1.7877 | 0.21209 | 1.237 | 0.42163
-1.7154 | 0.13899 | 1.2712 | 0.41864
-1.6431 | 0.067868 | 1.2923 | 0.41277
-1.5708 | 5.5511e-17 | 1.3 | 0.4069
-1.4985 | -0.067868 | 1.2923 | 0.39426
-1.4262 | -0.13899 | 1.2712 | 0.38162
-1.3539 | -0.21209 | 1.237 | 0.36676
-1.2816 | -0.28603 | 1.1906 | 0.35033
-1.2093 | -0.35981 | 1.1328 | 0.33362
-1.137 | -0.43261 | 1.0649 | 0.31561
-1.0647 | -0.50388 | 0.98826 | 0.29759
-0.99234 | -0.57335 | 0.90444 | 0.27989
-0.92004 | -0.64116 | 0.8152 | 0.2623
-0.84773 | -0.7079 | 0.72238 | 0.24491
-0.77542 | -0.77483 | 0.62793 | 0.22794
-0.70312 | -0.84406 | 0.53379 | 0.21097
-0.63081 | -0.91898 | 0.44192 | 0.13525
-0.55851 | -1.0049 | 0.35424 | 0.055174
-0.48869 | -1.1131 | 0.20494 | 0.032114
-0.41888 | -1.0542 | 0.15434 | 0.012679
-0.34907 | -0.98247 | 0.10967 | -0.0028213
-0.31416 | -0.94173 | 0.092489 | -0.0074129
-0.27925 | -0.89333 | 0.075974 | -0.011069
-0.24435 | -0.85472 | 0.060541 | -0.012501
-0.20944 | -0.82348 | 0.046412 | -0.011773
-0.17453 | -0.79541 | 0.03441 | -0.010821
-0.13963 | -0.6365 | 0.025482 | -0.027694
-0.10472 | -0.39095 | 0.01994 | -0.051068
-0.069813 | -0.13071 | 0.016534 | -0.071481
-0.034907 | 0.16173 | 0.01507 | -0.091788
-0.017453 | 0.31121 | 0.01477 | -0.10119
0 | 0.45956 | 0.014649 | -0.10988
0.017453 | 0.60566 | 0.014663 | -0.11776
0.034907 | 0.74868 | 0.014813 | -0.12477
0.05236 | 0.88862 | 0.015072 | -0.13098
0.069813 | 1.0254 | 0.01544 | -0.13648
0.087266 | 1.1588 | 0.015926 | -0.1413
0.10472 | 1.2882 | 0.016541 | -0.1454
0.12217 | 1.4128 | 0.017311 | -0.14875
0.13963 | 1.5309 | 0.01831 | -0.15118
0.15708 | 1.6406 | 0.019631 | -0.15262
0.17453 | 1.7393 | 0.021499 | -0.1531
0.19199 | 1.8197 | 0.024454 | -0.15254
0.20944 | 1.8706 | 0.029662 | -0.15121
0.22689 | 1.8922 | 0.0377 | -0.14969
0.24435 | 1.8791 | 0.048244 | -0.14562
0.2618 | 1.8811 | 0.058376 | -0.14358
0.27925 | 1.8636 | 0.069924 | -0.14095
0.31416 | 1.7332 | 0.10166 | -0.13711
0.34907 | 1.5936 | 0.13916 | -0.14082
0.41888 | 1.4671 | 0.21002 | -0.15693
0.48869 | 1.4483 | 0.282 | -0.17979
0.55851 | 1.4356 | 0.35424 | -0.20147
0.63081 | 1.3128 | 0.44192 | -0.22409
0.70312 | 1.2058 | 0.53379 | -0.24619
0.77542 | 1.1069 | 0.62793 | -0.26133
0.84773 | 1.0113 | 0.72238 | -0.27648
0.92004 | 0.91594 | 0.8152 | -0.29062
0.99234 | 0.81907 | 0.90444 | -0.30424
1.0647 | 0.71982 | 0.98826 | -0.31787
1.137 | 0.61801 | 1.0649 | -0.33154
1.2093 | 0.51401 | 1.1328 | -0.34522
1.2816 | 0.40862 | 1.1906 | -0.35846
1.3539 | 0.30299 | 1.237 | -0.37161
1.4262 | 0.19855 | 1.2712 | -0.38405
1.4985 | 0.096954 | 1.2923 | -0.39547
1.5708 | 8.3267e-17 | 1.3 | -0.4069
1.6431 | -0.067868 | 1.2923 | -0.41277
1.7154 | -0.13899 | 1.2712 | -0.41864
1.7877 | -0.21209 | 1.237 | -0.42163
1.86 | -0.28603 | 1.1906 | -0.42258
1.9323 | -0.35981 | 1.1328 | -0.42312
2.0046 | -0.43261 | 1.0649 | -0.42168
2.0769 | -0.50388 | 0.98826 | -0.42024
2.1492 | -0.57335 | 0.90444 | -0.42058
2.2216 | -0.64116 | 0.8152 | -0.4215
2.2939 | -0.7079 | 0.72238 | -0.42591
2.3662 | -0.77483 | 0.62793 | -0.43697
2.4385 | -0.84406 | 0.53379 | -0.44803
2.5108 | -0.91898 | 0.44192 | -0.46784
2.5831 | -1.0049 | 0.35424 | -0.4883
2.623 | -0.93316 | 0.30832 | -0.496
2.6629 | -0.86138 | 0.26453 | -0.47857
2.7028 | -0.7896 | 0.22313 | -0.46114
2.7427 | -0.71781 | 0.18439 | -0.4437
2.7826 | -0.64603 | 0.14856 | -0.42627
2.8224 | -0.57425 | 0.11586 | -0.4353
2.8623 | -0.50247 | 0.086508 | -0.45315
2.9022 | -0.43069 | 0.060678 | -0.471
2.9421 | -0.35891 | 0.051737 | -0.48884
2.982 | -0.28713 | 0.046531 | -0.45714
3.0219 | -0.21534 | 0.042446 | -0.34286
3.0618 | -0.14356 | 0.039509 | -0.22857
3.1017 | -0.071781 | 0.037739 | -0.11429
3.14 | 0 | 0.037148 | 0

## Blade Support Structure
Span position | Shear web-1 SS s-coord | Shear web-1 PS s-coord | Shear web-2 SS s-coord | Shear web-2 PS s-coord | Spar cap SS begin s-coord | Spar cap SS width [m] | Spar cap SS thick [m] | Spar cap PS begin s-coord | Spar cap PS width [m] | Spar cap PS thick [m] | LE reinf width [m] | LE reinf thick [m] | TE reinf width [m] | TE reinf thick [m]
0 | 0.20528 | 0.70808 | 0.20528 | 0.70808 | 0.17774 | 0.9 | 0.0001 | 0.68053 | 0.9 | 0.0001 | 0 | 0 | 0 | 0
0.02 | 0.20964 | 0.70374 | 0.20964 | 0.70374 | 0.18214 | 0.9 | 0.0018482 | 0.67624 | 0.9 | 0.0018482 | 0 | 0 | 0 | 0
0.04 | 0.2149 | 0.70087 | 0.2149 | 0.70087 | 0.1871 | 0.9 | 0.0056293 | 0.67307 | 0.9 | 0.0056293 | 0 | 0 | 0 | 0.00035348
0.06 | 0.22118 | 0.70077 | 0.22118 | 0.70077 | 0.1925 | 0.9 | 0.011724 | 0.67209 | 0.9 | 0.011724 | 0 | 0 | 0 | 0.0013335
0.08 | 0.22903 | 0.70146 | 0.22903 | 0.70146 | 0.19909 | 0.9 | 0.019595 | 0.67152 | 0.9 | 0.019595 | 0 | 0 | 0 | 0.0028193
0.1 | 0.26322 | 0.67687 | 0.21432 | 0.72595 | 0.20738 | 0.9 | 0.028705 | 0.66994 | 0.9 | 0.028705 | 0.8 | 0.003 | 1 | 0.0046903
0.125 | 0.27831 | 0.67271 | 0.22722 | 0.72442 | 0.21996 | 0.9 | 0.041017 | 0.66557 | 0.9 | 0.041017 | 0.8 | 0.0029643 | 1 | 0.0073868
0.15 | 0.29301 | 0.66659 | 0.24092 | 0.71954 | 0.2335 | 0.9 | 0.053377 | 0.65937 | 0.9 | 0.053377 | 0.8 | 0.0029286 | 1 | 0.010261
0.16903 | 0.30261 | 0.66151 | 0.25025 | 0.71475 | 0.24279 | 0.9 | 0.062173 | 0.65426 | 0.9 | 0.062173 | 0.8 | 0.0029014 | 1 | 0.012423
0.18807 | 0.3113 | 0.65702 | 0.25855 | 0.7107 | 0.25103 | 0.9 | 0.069925 | 0.64972 | 0.9 | 0.069925 | 0.8 | 0.0028742 | 1 | 0.014447
0.2071 | 0.31905 | 0.65279 | 0.26578 | 0.70699 | 0.25818 | 0.9 | 0.07617 | 0.64541 | 0.9 | 0.07617 | 0.8 | 0.002847 | 1 | 0.016229
0.22614 | 0.32561 | 0.64895 | 0.27171 | 0.70371 | 0.26402 | 0.9 | 0.080381 | 0.64145 | 0.9 | 0.080381 | 0.8 | 0.0028198 | 1 | 0.017807
0.24517 | 0.33102 | 0.6457 | 0.27628 | 0.70121 | 0.26847 | 0.9 | 0.083853 | 0.63805 | 0.9 | 0.083853 | 0.8 | 0.0027926 | 1 | 0.019333
0.26609 | 0.33626 | 0.64264 | 0.28034 | 0.69921 | 0.27237 | 0.9 | 0.087707 | 0.63478 | 0.9 | 0.087707 | 0.8 | 0.0027627 | 1 | 0.021151
0.28701 | 0.341 | 0.63973 | 0.28356 | 0.69773 | 0.27537 | 0.9 | 0.091175 | 0.63163 | 0.9 | 0.091175 | 0.8 | 0.0027328 | 1 | 0.022897
0.30793 | 0.3451 | 0.63722 | 0.28589 | 0.6969 | 0.27745 | 0.9 | 0.094203 | 0.62884 | 0.9 | 0.094203 | 0.8 | 0.002703 | 1 | 0.024504
0.32884 | 0.34887 | 0.63496 | 0.28765 | 0.69658 | 0.27893 | 0.9 | 0.096487 | 0.62627 | 0.9 | 0.096487 | 0.8 | 0.0026731 | 1 | 0.025764
0.35091 | 0.35253 | 0.63283 | 0.28914 | 0.69656 | 0.28011 | 0.9 | 0.098058 | 0.62383 | 0.9 | 0.098058 | 0.8 | 0.0026416 | 1 | 0.026663
0.37298 | 0.35604 | 0.63069 | 0.29056 | 0.69646 | 0.28124 | 0.9 | 0.098468 | 0.62138 | 0.9 | 0.098468 | 0.8 | 0.00261 | 1 | 0.026864
0.39505 | 0.35953 | 0.62842 | 0.2921 | 0.69608 | 0.28251 | 0.9 | 0.098068 | 0.61883 | 0.9 | 0.098068 | 0.8 | 0.0025785 | 1 | 0.026217
0.41711 | 0.36311 | 0.62598 | 0.29362 | 0.69565 | 0.28373 | 0.9 | 0.097241 | 0.61611 | 0.9 | 0.097241 | 0.8 | 0.002547 | 1 | 0.024941
0.43918 | 0.36671 | 0.62344 | 0.29504 | 0.69525 | 0.28484 | 0.9 | 0.095798 | 0.61327 | 0.9 | 0.095798 | 0.8 | 0.0025155 | 1 | 0.022801
0.45888 | 0.36979 | 0.62125 | 0.2961 | 0.69507 | 0.28561 | 0.9 | 0.094293 | 0.61082 | 0.9 | 0.094293 | 0.8 | 0.0024873 | 1 | 0.020648
0.47858 | 0.37275 | 0.61914 | 0.29695 | 0.69505 | 0.28617 | 0.9 | 0.09263 | 0.60843 | 0.9 | 0.09263 | 0.8 | 0.0024592 | 1 | 0.018387
0.49827 | 0.37558 | 0.61713 | 0.2976 | 0.69521 | 0.28651 | 0.9 | 0.090881 | 0.60614 | 0.9 | 0.090881 | 0.8 | 0.002431 | 1 | 0.016147
0.51797 | 0.37817 | 0.61533 | 0.29797 | 0.69562 | 0.28657 | 0.9 | 0.089192 | 0.60405 | 0.9 | 0.089192 | 0.8 | 0.0024029 | 1 | 0.014232
0.53767 | 0.38049 | 0.61377 | 0.29804 | 0.69631 | 0.28632 | 0.9 | 0.087535 | 0.60219 | 0.9 | 0.087535 | 0.8 | 0.0023748 | 1 | 0.012489
0.55778 | 0.38252 | 0.61246 | 0.29775 | 0.69732 | 0.28571 | 0.9 | 0.08584 | 0.60058 | 0.9 | 0.08584 | 0.8 | 0.002346 | 1 | 0.010627
0.57789 | 0.38447 | 0.61119 | 0.29733 | 0.69842 | 0.28496 | 0.9 | 0.084055 | 0.59899 | 0.9 | 0.084055 | 0.8 | 0.0023173 | 1 | 0.0087278
0.59799 | 0.38611 | 0.61021 | 0.29655 | 0.69986 | 0.28384 | 0.9 | 0.082132 | 0.59768 | 0.9 | 0.082132 | 0.8 | 0.0022886 | 1 | 0.0067837
0.6181 | 0.3876 | 0.60939 | 0.29553 | 0.70155 | 0.28247 | 0.9 | 0.080013 | 0.59651 | 0.9 | 0.080013 | 0.8 | 0.0022599 | 1 | 0.0049936
0.63821 | 0.3889 | 0.60878 | 0.29421 | 0.70356 | 0.28079 | 0.9 | 0.077661 | 0.59555 | 0.9 | 0.077661 | 0.8 | 0.0022311 | 1 | 0.0034432
0.65728 | 0.39013 | 0.60826 | 0.29279 | 0.70568 | 0.279 | 0.9 | 0.075202 | 0.59466 | 0.9 | 0.075202 | 0.79997 | 0.0022039 | 1 | 0.0022846
0.67636 | 0.39137 | 0.60777 | 0.2912 | 0.708 | 0.27704 | 0.9 | 0.072325 | 0.59379 | 0.9 | 0.072325 | 0.79981 | 0.0021766 | 1 | 0.0016092
0.69544 | 0.39261 | 0.60733 | 0.28942 | 0.71056 | 0.27485 | 0.9 | 0.068848 | 0.59293 | 0.9 | 0.068848 | 0.79836 | 0.0021494 | 1 | 0.001311
0.71451 | 0.39379 | 0.60697 | 0.28746 | 0.71333 | 0.27247 | 0.9 | 0.06416 | 0.59215 | 0.9 | 0.06416 | 0.79426 | 0.0021221 | 1 | 0.0010956
0.73359 | 0.39485 | 0.60674 | 0.28528 | 0.7163 | 0.26988 | 0.9 | 0.057833 | 0.59148 | 0.9 | 0.057833 | 0.78234 | 0.0020949 | 1 | 0.00092513
0.75267 | 0.39574 | 0.60656 | 0.28283 | 0.71946 | 0.267 | 0.9 | 0.050887 | 0.59086 | 0.9 | 0.050887 | 0.7628 | 0.0020676 | 1 | 0.00077534
0.77174 | 0.39642 | 0.60643 | 0.28007 | 0.72277 | 0.2638 | 0.9 | 0.043498 | 0.59028 | 0.9 | 0.043498 | 0.73606 | 0.0020404 | 1 | 0.00064926
0.8 | 0.3974 | 0.60602 | 0.27555 | 0.72787 | 0.2586 | 0.9 | 0.033023 | 0.58915 | 0.9 | 0.033023 | 0.7 | 0.002 | 1 | 0.00051345
0.81875 | 0.39806 | 0.60564 | 0.27213 | 0.73154 | 0.25467 | 0.9 | 0.027019 | 0.58822 | 0.9 | 0.027019 | 0 | 0 | 0 | 0.0004552
0.8375 | 0.39863 | 0.60516 | 0.26821 | 0.73554 | 0.25018 | 0.9 | 0.022342 | 0.58713 | 0.9 | 0.022342 | 0 | 0 | 0 | 0.0004409
0.85625 | 0.39915 | 0.60465 | 0.26375 | 0.74 | 0.2451 | 0.89999 | 0.018821 | 0.58593 | 0.89999 | 0.018821 | 0 | 0 | 0 | 0.00044294
0.875 | 0.39975 | 0.60403 | 0.25884 | 0.74488 | 0.2395 | 0.89989 | 0.015488 | 0.58455 | 0.89989 | 0.015488 | 0 | 0 | 0 | 0.00046636
0.89375 | 0.40048 | 0.60323 | 0.25344 | 0.7502 | 0.23337 | 0.89944 | 0.01239 | 0.58295 | 0.89944 | 0.01239 | 0 | 0 | 0 | 0.0005217
0.9125 | 0.40141 | 0.60218 | 0.24755 | 0.75599 | 0.22701 | 0.89595 | 0.0094879 | 0.58134 | 0.89595 | 0.0094879 | 0 | 0 | 0 | 0.00060175
0.93125 | 0.40257 | 0.60087 | 0.24107 | 0.76234 | 0.22115 | 0.8822 | 0.0068867 | 0.58057 | 0.8822 | 0.0068867 | 0 | 0 | 0 | 0.00070462
0.95 | 0.40394 | 0.59928 | 0.23383 | 0.7694 | 0.21822 | 0.83824 | 0.004684 | 0.58319 | 0.83824 | 0.004684 | 0 | 0 | 0 | 0.00083579
0.975 | 0.40602 | 0.5968 | 0.22274 | 0.78021 | 0.23032 | 0.6509 | 0.002512 | 0.60377 | 0.6509 | 0.002512 | 0 | 0 | 0 | 0.0010489
1 | 0.30965 | 0.6927 | 0.30965 | 0.6927 | 0.1687 | 0.294 | 0.001 | 0.55175 | 0.294 | 0.001 | 0 | 0 | 0 | 0

## Blade Shell Layup
Airfoil | circular
Pct Span | 0.0
Layer Name | Material | S-coord start | S-coord end | Thickness [mm] | Fiber direction [?]
UV_protection | Gelcoat | 0 | 1 | 0.5 | 0
Shell_skin | glass_triax | 0 | 1 | 50 | 0
Spar_cap_ss | CarbonUD | 0.17774 | 0.23283 | 0.1 | 0
Spar_cap_ps | CarbonUD | 0.68053 | 0.73563 | 0.1 | 0
LE_reinforcement | glass_uni | 0.5 | 0.5 | 0 | 0
TE_reinforcement | glass_uni | 1 | 1 | 0 | 0
TE_SS_filler | medium_density_foam | 1 | 0.17774 | 0 | 0
LE_SS_filler | medium_density_foam | 0.23283 | 0.5 | 0 | 0
LE_PS_filler | medium_density_foam | 0.5 | 0.68053 | 0 | 0
TE_PS_filler | medium_density_foam | 0.73563 | 1 | 0 | 0
Shell_skin_inner | glass_triax | 0 | 1 | 50 | 0
Airfoil | circular
Pct Span | 2.0
Layer Name | Material | S-coord start | S-coord end | Thickness [mm] | Fiber direction [?]
UV_protection | Gelcoat | 0 | 1 | 0.5 | 0
Shell_skin | glass_triax | 0 | 1 | 44.5913 | 0
Spar_cap_ss | CarbonUD | 0.18214 | 0.23715 | 1.8482 | 0
Spar_cap_ps | CarbonUD | 0.67624 | 0.73125 | 1.8482 | 0
LE_reinforcement | glass_uni | 0.5 | 0.5 | 0 | 0
TE_reinforcement | glass_uni | 1 | 1 | 0 | 0
TE_SS_filler | medium_density_foam | 1 | 0.18214 | 0 | 0
LE_SS_filler | medium_density_foam | 0.23715 | 0.5 | 0 | 0
LE_PS_filler | medium_density_foam | 0.5 | 0.67624 | 0 | 0
TE_PS_filler | medium_density_foam | 0.73125 | 1 | 0 | 0
Shell_skin_inner | glass_triax | 0 | 1 | 44.5913 | 0
Airfoil | SNL-FFA-W3-500
Pct Span | 15.0
Layer Name | Material | S-coord start | S-coord end | Thickness [mm] | Fiber direction [?]
UV_protection | Gelcoat | 0 | 1 | 0.5 | 0
Shell_skin | glass_triax | 0 | 1 | 12.9357 | 0
Spar_cap_ss | CarbonUD | 0.2335 | 0.30032 | 53.3773 | 0
Spar_cap_ps | CarbonUD | 0.65937 | 0.72619 | 53.3773 | 0
LE_reinforcement | glass_uni | 0.47076 | 0.53016 | 2.9286 | 0
TE_reinforcement | glass_uni | 0.96288 | 0.037124 | 10.2609 | 0
TE_SS_filler | medium_density_foam | 0.037124 | 0.2335 | 56.0714 | 0
LE_SS_filler | medium_density_foam | 0.30032 | 0.47076 | 56.0714 | 0
LE_PS_filler | medium_density_foam | 0.53016 | 0.65937 | 56.0714 | 0
TE_PS_filler | medium_density_foam | 0.72619 | 0.96288 | 56.0714 | 0
Shell_skin_inner | glass_triax | 0 | 1 | 12.9357 | 0
Airfoil | FFA-W3-360
Pct Span | 24.517031675566095
Layer Name | Material | S-coord start | S-coord end | Thickness [mm] | Fiber direction [?]
UV_protection | Gelcoat | 0 | 1 | 0.5 | 0
Shell_skin | glass_triax | 0 | 1 | 3.0103 | 0
Spar_cap_ss | CarbonUD | 0.26847 | 0.33879 | 83.8534 | 0
Spar_cap_ps | CarbonUD | 0.63805 | 0.70837 | 83.8534 | 0
LE_reinforcement | glass_uni | 0.46841 | 0.53091 | 2.7926 | 0
TE_reinforcement | glass_uni | 0.96094 | 0.039062 | 19.3326 | 0
TE_SS_filler | medium_density_foam | 0.039062 | 0.26847 | 48.5938 | 0
LE_SS_filler | medium_density_foam | 0.33879 | 0.46841 | 48.5938 | 0
LE_PS_filler | medium_density_foam | 0.53091 | 0.63805 | 48.5938 | 0
TE_PS_filler | medium_density_foam | 0.70837 | 0.96094 | 48.5938 | 0
Shell_skin_inner | glass_triax | 0 | 1 | 3.0103 | 0
Airfoil | FFA-W3-330blend
Pct Span | 32.884395064724345
Layer Name | Material | S-coord start | S-coord end | Thickness [mm] | Fiber direction [?]
UV_protection | Gelcoat | 0 | 1 | 0.5 | 0
Shell_skin | glass_triax | 0 | 1 | 2.0017 | 0
Spar_cap_ss | CarbonUD | 0.27893 | 0.35754 | 96.4867 | 0
Spar_cap_ps | CarbonUD | 0.62627 | 0.70488 | 96.4867 | 0
LE_reinforcement | glass_uni | 0.46375 | 0.53362 | 2.6731 | 0
TE_reinforcement | glass_uni | 0.95633 | 0.043673 | 25.7642 | 0
TE_SS_filler | medium_density_foam | 0.043673 | 0.27893 | 42.0194 | 0
LE_SS_filler | medium_density_foam | 0.35754 | 0.46375 | 42.0194 | 0
LE_PS_filler | medium_density_foam | 0.53362 | 0.62627 | 42.0194 | 0
TE_PS_filler | medium_density_foam | 0.70488 | 0.95633 | 42.0194 | 0
Shell_skin_inner | glass_triax | 0 | 1 | 2.0017 | 0
Airfoil | FFA-W3-301
Pct Span | 43.91793464459161
Layer Name | Material | S-coord start | S-coord end | Thickness [mm] | Fiber direction [?]
UV_protection | Gelcoat | 0 | 1 | 0.5 | 0
Shell_skin | glass_triax | 0 | 1 | 2 | 0
Spar_cap_ss | CarbonUD | 0.28484 | 0.3768 | 95.7977 | 0
Spar_cap_ps | CarbonUD | 0.61327 | 0.70523 | 95.7977 | 0
LE_reinforcement | glass_uni | 0.4575 | 0.53924 | 2.5155 | 0
TE_reinforcement | glass_uni | 0.94891 | 0.051085 | 22.8007 | 0
TE_SS_filler | medium_density_foam | 0.051085 | 0.28484 | 33.3502 | 0
LE_SS_filler | medium_density_foam | 0.3768 | 0.4575 | 33.3502 | 0
LE_PS_filler | medium_density_foam | 0.53924 | 0.61327 | 33.3502 | 0
TE_PS_filler | medium_density_foam | 0.70523 | 0.94891 | 33.3502 | 0
Shell_skin_inner | glass_triax | 0 | 1 | 2 | 0
Airfoil | FFA-W3-270blend
Pct Span | 53.76714071084352
Layer Name | Material | S-coord start | S-coord end | Thickness [mm] | Fiber direction [?]
UV_protection | Gelcoat | 0 | 1 | 0.5 | 0
Shell_skin | glass_triax | 0 | 1 | 2 | 0
Spar_cap_ss | CarbonUD | 0.28632 | 0.39203 | 87.5352 | 0
Spar_cap_ps | CarbonUD | 0.60219 | 0.7079 | 87.5352 | 0
LE_reinforcement | glass_uni | 0.45256 | 0.54652 | 2.3748 | 0
TE_reinforcement | glass_uni | 0.94127 | 0.058726 | 12.4895 | 0
TE_SS_filler | medium_density_foam | 0.058726 | 0.28632 | 25.6115 | 0
LE_SS_filler | medium_density_foam | 0.39203 | 0.45256 | 25.6115 | 0
LE_PS_filler | medium_density_foam | 0.54652 | 0.60219 | 25.6115 | 0
TE_PS_filler | medium_density_foam | 0.7079 | 0.94127 | 25.6115 | 0
Shell_skin_inner | glass_triax | 0 | 1 | 2 | 0
Airfoil | FFA-W3-241
Pct Span | 63.82076569163737
Layer Name | Material | S-coord start | S-coord end | Thickness [mm] | Fiber direction [?]
UV_protection | Gelcoat | 0 | 1 | 0.5 | 0
Shell_skin | glass_triax | 0 | 1 | 2 | 0
Spar_cap_ss | CarbonUD | 0.28079 | 0.40214 | 77.6606 | 0
Spar_cap_ps | CarbonUD | 0.59555 | 0.7169 | 77.6606 | 0
LE_reinforcement | glass_uni | 0.44709 | 0.55496 | 2.2311 | 0
TE_reinforcement | glass_uni | 0.93258 | 0.06742 | 3.4432 | 0
TE_SS_filler | medium_density_foam | 0.06742 | 0.28079 | 17.7123 | 0
LE_SS_filler | medium_density_foam | 0.40214 | 0.44709 | 17.7123 | 0
LE_PS_filler | medium_density_foam | 0.55496 | 0.59555 | 17.7123 | 0
TE_PS_filler | medium_density_foam | 0.7169 | 0.93258 | 17.7123 | 0
Shell_skin_inner | glass_triax | 0 | 1 | 2 | 0
Airfoil | FFA-W3-211
Pct Span | 77.17438522715817
Layer Name | Material | S-coord start | S-coord end | Thickness [mm] | Fiber direction [?]
UV_protection | Gelcoat | 0 | 1 | 0.5 | 0
Shell_skin | glass_triax | 0 | 1 | 2 | 0
Spar_cap_ss | CarbonUD | 0.2638 | 0.41269 | 43.4979 | 0
Spar_cap_ps | CarbonUD | 0.59028 | 0.73917 | 43.4979 | 0
LE_reinforcement | glass_uni | 0.44228 | 0.56404 | 2.0404 | 0
TE_reinforcement | glass_uni | 0.91729 | 0.082715 | 0.64926 | 0
TE_SS_filler | medium_density_foam | 0.082715 | 0.2638 | 7.2201 | 0
LE_SS_filler | medium_density_foam | 0.41269 | 0.44228 | 7.2201 | 0
LE_PS_filler | medium_density_foam | 0.56404 | 0.59028 | 7.2201 | 0
TE_PS_filler | medium_density_foam | 0.73917 | 0.91729 | 7.2201 | 0
Shell_skin_inner | glass_triax | 0 | 1 | 2 | 0
Airfoil | FFA-W3-211
Pct Span | 100.0
Layer Name | Material | S-coord start | S-coord end | Thickness [mm] | Fiber direction [?]
UV_protection | Gelcoat | 0 | 1 | 0.5 | 0
Shell_skin | glass_triax | 0 | 1 | 1 | 0
Spar_cap_ss | CarbonUD | 0.1687 | 0.4506 | 1 | 0
Spar_cap_ps | CarbonUD | 0.55175 | 0.83365 | 1 | 0
LE_reinforcement | glass_uni | 0.50316 | 0.50316 | 0 | 0
TE_reinforcement | glass_uni | 1 | 1 | 0 | 0
TE_SS_filler | medium_density_foam | 1 | 0.1687 | 0 | 0
LE_SS_filler | medium_density_foam | 0.4506 | 0.50316 | 0 | 0
LE_PS_filler | medium_density_foam | 0.50316 | 0.55175 | 0 | 0
TE_PS_filler | medium_density_foam | 0.83365 | 1 | 0 | 0
Shell_skin_inner | glass_triax | 0 | 1 | 1 | 0

## Shear Web Layup
Airfoil | circular
Pct Span | 0.0
Shear web | Layer Name | Material | Thickness [mm] | Fiber direction [?]
Airfoil | circular
Pct Span | 2.0
Shear web | Layer Name | Material | Thickness [mm] | Fiber direction [?]
Airfoil | SNL-FFA-W3-500
Pct Span | 15.0
Shear web | Layer Name | Material | Thickness [mm] | Fiber direction [?]
web0 | web0_skinLE | glass_biax | 1.9118 | 0
web0 | web0_filler | medium_density_foam | 40.7647 | 0
web0 | web0_skinTE | glass_biax | 1.9118 | 0
web1 | web1_skinLE | glass_biax | 1.9118 | 0
web1 | web1_filler | medium_density_foam | 40.7647 | 0
web1 | web1_skinTE | glass_biax | 1.9118 | 0
Airfoil | FFA-W3-360
Pct Span | 24.517031675566095
Shear web | Layer Name | Material | Thickness [mm] | Fiber direction [?]
web0 | web0_skinLE | glass_biax | 1.7438 | 0
web0 | web0_filler | medium_density_foam | 36.51 | 0
web0 | web0_skinTE | glass_biax | 1.7438 | 0
web1 | web1_skinLE | glass_biax | 1.7438 | 0
web1 | web1_filler | medium_density_foam | 36.51 | 0
web1 | web1_skinTE | glass_biax | 1.7438 | 0
Airfoil | FFA-W3-330blend
Pct Span | 32.884395064724345
Shear web | Layer Name | Material | Thickness [mm] | Fiber direction [?]
web0 | web0_skinLE | glass_biax | 1.5962 | 0
web0 | web0_filler | medium_density_foam | 32.7693 | 0
web0 | web0_skinTE | glass_biax | 1.5962 | 0
web1 | web1_skinLE | glass_biax | 1.5962 | 0
web1 | web1_filler | medium_density_foam | 32.7693 | 0
web1 | web1_skinTE | glass_biax | 1.5962 | 0
Airfoil | FFA-W3-301
Pct Span | 43.91793464459161
Shear web | Layer Name | Material | Thickness [mm] | Fiber direction [?]
web0 | web0_skinLE | glass_biax | 1.4014 | 0
web0 | web0_filler | medium_density_foam | 27.8367 | 0
web0 | web0_skinTE | glass_biax | 1.4014 | 0
web1 | web1_skinLE | glass_biax | 1.4014 | 0
web1 | web1_filler | medium_density_foam | 27.8367 | 0
web1 | web1_skinTE | glass_biax | 1.4014 | 0
Airfoil | FFA-W3-270blend
Pct Span | 53.76714071084352
Shear web | Layer Name | Material | Thickness [mm] | Fiber direction [?]
web0 | web0_skinLE | glass_biax | 1.2276 | 0
web0 | web0_filler | medium_density_foam | 23.4335 | 0
web0 | web0_skinTE | glass_biax | 1.2276 | 0
web1 | web1_skinLE | glass_biax | 1.2276 | 0
web1 | web1_filler | medium_density_foam | 23.4335 | 0
web1 | web1_skinTE | glass_biax | 1.2276 | 0
Airfoil | FFA-W3-241
Pct Span | 63.82076569163737
Shear web | Layer Name | Material | Thickness [mm] | Fiber direction [?]
web0 | web0_skinLE | glass_biax | 1.0502 | 0
web0 | web0_filler | medium_density_foam | 18.939 | 0
web0 | web0_skinTE | glass_biax | 1.0502 | 0
web1 | web1_skinLE | glass_biax | 1.0502 | 0
web1 | web1_filler | medium_density_foam | 18.939 | 0
web1 | web1_skinTE | glass_biax | 1.0502 | 0
Airfoil | FFA-W3-211
Pct Span | 77.17438522715817
Shear web | Layer Name | Material | Thickness [mm] | Fiber direction [?]
web0 | web0_skinLE | glass_biax | 0.81457 | 0
web0 | web0_filler | medium_density_foam | 12.9691 | 0
web0 | web0_skinTE | glass_biax | 0.81457 | 0
web1 | web1_skinLE | glass_biax | 0.81457 | 0
web1 | web1_filler | medium_density_foam | 12.9691 | 0
web1 | web1_skinTE | glass_biax | 0.81457 | 0
Airfoil | FFA-W3-211
Pct Span | 100.0
Shear web | Layer Name | Material | Thickness [mm] | Fiber direction [?]

## Blade Structural Properties
BeamDyn Coordinate System (see https://wind.nrel.gov/nwtc/docs/BeamDyn_Manual.pdf)
| Mass per unit length [kg/m] | Mass center (chordwise), m | Mass center (thickness), m | Neutral axes (chordwise), m | Neutral axes (thickness), m | Geometric center (chordwise), m | Geometric center (thickness), m | Shear center (chordwise), m | Shear center (thickness), m | M_11 | M_12 | M_13 | M_14 | M_15 | M_16 | M_22 | M_23 | M_24 | M_25 | M_26 | M_33 | M_34 | M_35 | M_36 | M_44 | M_45 | M_46 | M_55 | M_56 | M_66 | K_11 | K_12 | K_13 | K_14 | K_15 | K_16 | K_22 | K_23 | K_24 | K_25 | K_26 | K_33 | K_34 | K_35 | K_36 | K_44 | K_45 | K_46 | K_55 | K_56 | K_66
0 | 3118.7568 | -0.023622 | 0.0039553 | -0.023527 | -0.0042537 | -0.02361 | 9.7097e-05 | -0.023423 | 0.0015931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.1 | 1641.4253 | 0.2851 | 0.012988 | 0.24467 | 0.013386 | 0.21225 | 0.0083717 | 0.11093 | 0.011653 | 3118.7568 | 0 | 0 | 0 | 0 | 73.6711 | 3118.7568 | 0 | 0 | 0 | 12.3355 | 3118.7568 | -73.6711 | -12.3355 | 0 | 10137.4509 | -2.9839 | 0 | 10144.6924 | 0 | 20282.1433 | 6684511012.2 | 8282603.4447 | 0 | 0 | 0 | 156583554.03 | 6666911192 | 0 | 0 | 0 | 10815344.599 | 46105432460 | -1085924712.6 | 344944729.75 | 0 | 149015710680 | -185870689.76 | 0 | 149654745880 | 0 | 87417078218
0.2 | 594.4032 | 0.60878 | 0.026235 | 0.2571 | 0.013716 | 0.48498 | 0.025947 | -0.067533 | 0.021179 | 1641.4253 | 0 | 0 | 0 | 0 | -467.9671 | 1641.4253 | 0 | 0 | 0 | 21.3193 | 1641.4253 | 467.9671 | -21.3193 | 0 | 4687.2399 | -111.5678 | 0 | 2756.8507 | 0 | 7444.0906 | 2186909647.4 | 12054851.771 | -56949936.183 | -132188033.14 | 12886127.438 | -243076328.69 | 4014794571.8 | 2125901.0041 | -248610.2274 | -6340359.2479 | 45453360.969 | 26758272040 | 6535075230.9 | -363532056.05 | 134267268.49 | 67178451257 | -5087441448.6 | 239444687.27 | 52574877624 | -5060163.1715 | 25258767243
0.3 | 431.3459 | 0.73158 | 0.02826 | 0.24625 | 0.012312 | 0.62462 | 0.035212 | 0.011482 | 0.076575 | 594.4032 | 0 | 0 | 0 | 0 | -361.8593 | 594.4032 | 0 | 0 | 0 | 15.594 | 594.4032 | 361.8593 | -15.594 | 0 | 1690.7313 | -64.43 | 0 | 464.3725 | 0 | 2155.1038 | 311217749.31 | 26817516.054 | -50145035.382 | -125455111.87 | 16554435.932 | 19745786.258 | 1112398966.7 | -3990444.1913 | 16932256.592 | -90343485.94 | 25431896.026 | 18833824665 | 4865944881.3 | -293544519.38 | 199800615.8 | 25181649605 | -2898484063.7 | 321152076.02 | 21668899237 | -11519599.54 | 2676554986.7
0.4 | 400.6542 | 0.72367 | 0.017319 | 0.24481 | 0.005416 | 0.63154 | 0.025489 | 0.0022937 | 0.02726 | 431.3459 | 0 | 0 | 0 | 0 | -315.563 | 431.3459 | 0 | 0 | 0 | 12.1898 | 431.3459 | 315.563 | -12.1898 | 0 | 1167.0673 | -32.8702 | 0 | 198.4781 | 0 | 1365.5454 | 129306294.29 | 9669205.3012 | -37530042.859 | -82195857.531 | 4332837.5072 | -1774077.408 | 478621831.87 | -1012733.3391 | 1941554.9037 | -49140622.939 | 36516816.365 | 19950618395 | 4913221990.5 | -247743569.47 | 121437996.67 | 20126450646 | -1004877842.6 | 238919968.96 | 13090680087 | -4920516.1909 | 632691713.86
0.501 | 326.4021 | 0.50518 | 0.015683 | 0.14213 | 0.0045156 | 0.53469 | 0.022719 | -0.032465 | 0.04717 | 400.6542 | 0 | 0 | 0 | 0 | -289.9428 | 400.6542 | 0 | 0 | 0 | 6.9389 | 400.6542 | 289.9428 | -6.9389 | 0 | 917.3048 | -17.8436 | 0 | 118.0017 | 0 | 1035.3065 | 92909674.498 | 3521965.3615 | -24043410.385 | -48673581.683 | 868009.0887 | -496109.9098 | 403258064.62 | 8229190.3279 | 23881656.876 | -22635477.434 | 11163780.417 | 17315014790 | 4378437901.5 | -125131898.45 | 56586326.929 | 17026103930 | -288717794.13 | 127431207.84 | 8420233135.3 | -2131524.0819 | 353914938.41
0.6 | 269.0288 | 0.33569 | 0.022584 | 0.079274 | 0.016125 | 0.41026 | 0.028317 | -0.086609 | -0.0060656 | 326.4021 | 0 | 0 | 0 | 0 | -164.8911 | 326.4021 | 0 | 0 | 0 | 5.1188 | 326.4021 | 164.8911 | -5.1188 | 0 | 455.0603 | -9.3375 | 0 | 65.2595 | 0 | 520.3198 | 67027256.605 | 5127744.0516 | -9369801.7857 | -16672295.204 | 239382.0965 | 2342659.2609 | 405826815.83 | 392729.9018 | -610300.0158 | -8639536.6513 | 19306513.018 | 18562127095 | 2638064282.2 | -83140138.715 | 23684787.073 | 8422853961.5 | -108545875.4 | 35973407.019 | 4830851410.1 | -629810.3509 | 202338107.16
0.7 | 214.0096 | 0.21206 | 0.032467 | 0.039186 | 0.029768 | 0.2723 | 0.035727 | -0.14531 | -0.012916 | 269.0288 | 0 | 0 | 0 | 0 | -90.3091 | 269.0288 | 0 | 0 | 0 | 6.0758 | 269.0288 | 90.3091 | -6.0758 | 0 | 222.7611 | -4.9147 | 0 | 35.2238 | 0 | 257.9849 | 47134518.944 | 4583586.7774 | -3450141.4772 | -5965192.045 | 80625.502 | 4039212.3509 | 442686951.74 | 5005439.7124 | 2209061.7015 | -3483114.1856 | -2281089.4644 | 15897450963 | 1274262048.2 | -265104405.24 | 8150216.0684 | 4118966033.2 | -36146371.946 | 9628989.9203 | 2672725270.7 | -274690.9217 | 113016897.31
0.8 | 128.3181 | 0.19331 | 0.036745 | 0.037138 | 0.036101 | 0.19041 | 0.038128 | -0.19354 | 0.025552 | 214.0096 | 0 | 0 | 0 | 0 | -45.3821 | 214.0096 | 0 | 0 | 0 | 6.9481 | 214.0096 | 45.3821 | -6.9481 | 0 | 105.3149 | -2.4747 | 0 | 17.9409 | 0 | 123.2558 | 32645074.717 | 4708090.3234 | -1579710.7545 | -3492673.3637 | 56474.1949 | 4675749.1476 | 537685540.33 | 13797088.524 | 2222172.0378 | -2036087.5555 | -6252282.2996 | 13813317641 | 551739288.26 | -416046032.68 | 4715325.9101 | 2054044473 | -20183490.104 | 3507292.2151 | 1375336683.8 | -197540.6684 | 62690018.996
0.9 | 54.7854 | 0.18458 | 0.031928 | 0.048184 | 0.0319 | 0.1323 | 0.031774 | -0.099925 | 0.0097532 | 128.3181 | 0 | 0 | 0 | 0 | -24.8049 | 128.3181 | 0 | 0 | 0 | 4.715 | 128.3181 | 24.8049 | -4.715 | 0 | 54.5149 | -1.1944 | 0 | 6.7938 | 0 | 61.3087 | 23581503.154 | 3401417.4585 | -589441.9879 | -1516421.0406 | 16857.4289 | 4648890.222 | 414777278.73 | 7241262.4955 | 515203.8194 | -535017.653 | 11258858.293 | 7377092335.6 | 277103510.11 | -267421055.85 | 2024672.3504 | 1087165393.6 | -5050906.5741 | 1191449.1647 | 476054705.48 | -90807.0657 | 36020583.576
1 | 26.3851 | 0.17435 | 0.023945 | 0.13357 | 0.024002 | 0.16944 | 0.023955 | -0.27609 | 0.027785 | 54.7854 | 0 | 0 | 0 | 0 | -10.1123 | 54.7854 | 0 | 0 | 0 | 1.7492 | 54.7854 | 10.1123 | -1.7492 | 0 | 17.6567 | -0.40994 | 0 | 1.9198 | 0 | 19.5766 | 12259043.514 | 1479023.0908 | 96736.5628 | 206764.1481 | -4034.9513 | 1239327.4597 | 184909259.66 | -823506.4302 | -98457.8656 | 38719.615 | 1951332.7378 | 2748377656.9 | 133176298.12 | -87992864.629 | -238360.209 | 374266159.53 | -5113919.7981 | -124354.7735 | 119795396.38 | 8031.1395 | 12388624.758

## Tower Properties
Location | Height [m] | OD [m] | Thickness [mm] | Mass Density [kg/m] | Fore-aft inertia [kg.m] | Side-side inertia [kg.m] | Fore-aft stiffness [N.m^2] | Side-side stiffness [N.m^2] | Torsional stiffness [N.m^2] | Axial stiffness [N]
Monopile start | -75 | 10 | 55.341 | 13572.393 | 167787.5303 | 167787.5303 | 4.2748e+12 | 4.2748e+12 | 3.3899e+12 | 345793453239.6111
Mud line | -30 | 10 | 55.341 | 13572.393 | 167787.5303 | 167787.5303 | 4.2748e+12 | 4.2748e+12 | 3.3899e+12 | 345793453239.6111
| -29.999 | 10 | 55.341 | 13572.393 | 167787.5303 | 167787.5303 | 4.2748e+12 | 4.2748e+12 | 3.3899e+12 | 345793453239.6111
| -25 | 10 | 55.341 | 13572.393 | 167787.5303 | 167787.5303 | 4.2748e+12 | 4.2748e+12 | 3.3899e+12 | 345793453239.6111
| -24.999 | 10 | 53.449 | 13110.8735 | 162143.3749 | 162143.3749 | 4.131e+12 | 4.131e+12 | 3.2759e+12 | 334034993868.8577
| -20 | 10 | 53.449 | 13110.8735 | 162143.3749 | 162143.3749 | 4.131e+12 | 4.131e+12 | 3.2759e+12 | 334034993868.8577
| -19.999 | 10 | 51.509 | 12637.4619 | 156349.2986 | 156349.2986 | 3.9834e+12 | 3.9834e+12 | 3.1589e+12 | 321973551662.2469
| -15 | 10 | 51.509 | 12637.4619 | 156349.2986 | 156349.2986 | 3.9834e+12 | 3.9834e+12 | 3.1589e+12 | 321973551662.2469
| -14.999 | 10 | 49.527 | 12153.6095 | 150422.7419 | 150422.7419 | 3.8324e+12 | 3.8324e+12 | 3.0391e+12 | 309646101275.3164
| -10 | 10 | 49.527 | 12153.6095 | 150422.7419 | 150422.7419 | 3.8324e+12 | 3.8324e+12 | 3.0391e+12 | 309646101275.3164
| -9.999 | 10 | 47.517 | 11662.7237 | 144405.1855 | 144405.1855 | 3.6791e+12 | 3.6791e+12 | 2.9175e+12 | 297139457640.3081
| -5 | 10 | 47.517 | 11662.7237 | 144405.1855 | 144405.1855 | 3.6791e+12 | 3.6791e+12 | 2.9175e+12 | 297139457640.3081
| -4.999 | 10 | 45.517 | 11174.0824 | 138410.2906 | 138410.2906 | 3.5264e+12 | 3.5264e+12 | 2.7964e+12 | 284689996998.3259
Water line | 0 | 10 | 45.517 | 11174.0824 | 138410.2906 | 138410.2906 | 3.5264e+12 | 3.5264e+12 | 2.7964e+12 | 284689996998.3259
| 0.001 | 10 | 43.527 | 10687.6884 | 132438.1602 | 132438.1602 | 3.3742e+12 | 3.3742e+12 | 2.6758e+12 | 272297794747.5821
| 5 | 10 | 43.527 | 10687.6884 | 132438.1602 | 132438.1602 | 3.3742e+12 | 3.3742e+12 | 2.6758e+12 | 272297794747.5821
| 5.001 | 10 | 42.242 | 10373.5062 | 128577.9605 | 128577.9605 | 3.2759e+12 | 3.2759e+12 | 2.5978e+12 | 264293150601.7534
| 10 | 10 | 42.242 | 10373.5062 | 128577.9605 | 128577.9605 | 3.2759e+12 | 3.2759e+12 | 2.5978e+12 | 264293150601.7534
| 10.001 | 10 | 41.058 | 10083.9463 | 125018.5115 | 125018.5115 | 3.1852e+12 | 3.1852e+12 | 2.5259e+12 | 256915828495.4436
Tower start | 15 | 10 | 41.058 | 10083.9463 | 125018.5115 | 125018.5115 | 3.1852e+12 | 3.1852e+12 | 2.5259e+12 | 256915828495.4436
| 15.001 | 10 | 39.496 | 9701.8366 | 120318.7823 | 120318.7823 | 3.0654e+12 | 3.0654e+12 | 2.4309e+12 | 247180551443.4128
| 28 | 10 | 39.496 | 9701.8366 | 120318.7823 | 120318.7823 | 3.0654e+12 | 3.0654e+12 | 2.4309e+12 | 247180551443.4128
| 28.001 | 10 | 36.456 | 8957.8212 | 111159.3251 | 111159.3251 | 2.8321e+12 | 2.8321e+12 | 2.2458e+12 | 228224743138.6868
| 41 | 9.926 | 36.456 | 8891.2907 | 108700.9302 | 108700.9302 | 2.7695e+12 | 2.7695e+12 | 2.1962e+12 | 226529700592.3543
| 41.001 | 9.926 | 33.779 | 8240.6246 | 100800.5323 | 100800.5323 | 2.5682e+12 | 2.5682e+12 | 2.0366e+12 | 209952218050.8469
| 54 | 9.443 | 33.779 | 7838.2658 | 86744.6973 | 86744.6973 | 2.2101e+12 | 2.2101e+12 | 1.7526e+12 | 199701039744.324
| 54.001 | 9.443 | 32.192 | 7471.2695 | 82711.0097 | 82711.0097 | 2.1073e+12 | 2.1073e+12 | 1.6711e+12 | 190350814904.366
| 67 | 8.833 | 32.192 | 6986.9886 | 67647.3754 | 67647.3754 | 1.7235e+12 | 1.7235e+12 | 1.3667e+12 | 178012448518.4323
| 67.001 | 8.833 | 30.708 | 6666.0234 | 64561.5092 | 64561.5092 | 1.6449e+12 | 1.6449e+12 | 1.3044e+12 | 169834990660.5962
| 80 | 8.151 | 30.708 | 6149.5411 | 50687.6579 | 50687.6579 | 1.2914e+12 | 1.2914e+12 | 1.0241e+12 | 156676206149.6397
| 80.001 | 8.151 | 29.101 | 5828.8788 | 48063.5433 | 48063.5433 | 1.2245e+12 | 1.2245e+12 | 971067257127.3551 | 148506466847.5468
| 93 | 7.39 | 29.101 | 5282.7286 | 35779.7103 | 35779.7103 | 911584975111.2295 | 911584975111.2295 | 722886885263.205 | 134591812002.5436
| 93.001 | 7.39 | 27.213 | 4941.2655 | 33484.0982 | 33484.0982 | 853098044023.8868 | 853098044023.8868 | 676506748910.9423 | 125892114148.985
| 106 | 6.909 | 27.213 | 4618.4599 | 27341.1284 | 27341.1284 | 696589258960.8757 | 696589258960.8757 | 552395282355.9745 | 117667768272.1226
| 106.001 | 6.909 | 24.009 | 4076.5895 | 24155.6665 | 24155.6665 | 615430994795.9966 | 615430994795.9966 | 488036778873.2252 | 103862152005.8945
| 119 | 6.748 | 24.009 | 3981.2617 | 22500.4146 | 22500.4146 | 573258971811.3063 | 573258971811.3063 | 454594364646.3658 | 101433418769.6498
| 119.001 | 6.748 | 20.826 | 3455.0796 | 19545.0845 | 19545.0845 | 497963935464.2214 | 497963935464.2214 | 394885400823.1276 | 88027505148.3052
| 132 | 6.572 | 20.826 | 3364.6859 | 18050.8309 | 18050.8309 | 459893782098.6934 | 459893782098.6934 | 364695769204.2639 | 85724481485.4559
| 132.001 | 6.572 | 23.998 | 3875.2826 | 20770.0162 | 20770.0162 | 529172386815.796 | 529172386815.796 | 419633702744.9262 | 98733315436.6877
Tower top | 144.582 | 6.5 | 23.998 | 3832.6711 | 20092.3844 | 20092.3844 | 511907882162.8501 | 511907882162.8501 | 405942950555.1401 | 97647671493.4752

## Material Properties
Material name | Density [kg/m^3] | Fiber vol fraction | Young Modulus E_1 [MPa] | Young Modulus E_2 [MPa] | Young Modulus E_3 [MPa] | Shear Modulus G_1 [MPa] | Shear Modulus G_2 [MPa] | Shear Modulus G_3 [MPa] | Poisson ratio nu_1 | Poisson ratio nu_2 | Poisson ratio nu_3 | Tensile failure Xt_1 [MPa] | Tensile failure Xt_2 [MPa] | Tensile failure Xt_3 [MPa] | Compressive failure Xc_1 [MPa] | Compressive failure Xc_2 [MPa] | Compressive failure Xc_3 [MPa] | Description | Reference
Gelcoat | 1235 |  | 3440 | 3440 | 3440 | 1323 | 1323 | 1323 | 0.3 | 0.3 | 0.3 | 7.4e-05 | 7.4e-05 | 7.4e-05 | 8.7e-05 | 8.7e-05 | 8.7e-05
Steel | 7850 |  | 200000 | 200000 | 200000 | 79300 | 79300 | 79300 | 0.265 | 0.265 | 0.265 | 1120 | 1120 | 1120 | 2160 | 2160 | 2160
glass_uni | 1940 | 0.57 | 44600 | 17000 | 16700 | 3270 | 3480 | 3500 | 0.262 | 0.35 | 0.264 | 1060 | 66.3 | 26.6 | 826 | 196 | 197 | Vectorply E-LT-5500, Epikote MGS RIMR 135/Epicure MGS RIMH 1366 epoxy | MSU composites database 3D property tests, Engineering Mechanics of Composite Materials, Daniel, I & Ishai, O., 1994, pg. 34
CarbonUD | 1220 |  | 114500 | 8390 | 8390 | 5990 | 5990 | 5990 | 0.27 | 0.27 | 0.27 | 0 | 0 | 0 | 0 | 0 | 0
glass_biax | 1940 | 0.57 | 11100 | 11100 | 16700 | 13530 | 3490 | 3490 | 0.5 | 0 | 0.066 | 54.47 | 54.47 | 26.6 | 74.1 | 74.1 | 197 | Vectorply E-LT-5500, Epikote MGS RIMR 135/Epicure MGS RIMH 1366 epoxy | MSU composites database 3D property tests, Engineering Mechanics of Composite Materials, Daniel, I & Ishai, O., 1994, pg. 34
glass_triax | 1940 | 0.57 | 28700 | 16600 | 16700 | 8400 | 3490 | 3490 | 0.5 | 0 | 0.17 | 54.5 | 54.5 | 26.6 | 74.1 | 74.1 | 197 | Vectorply E-LT-5500, Epikote MGS RIMR 135/Epicure MGS RIMH 1366 epoxy | MSU composites database 3D property tests, Engineering Mechanics of Composite Materials, Daniel, I & Ishai, O., 1994, pg. 34
balsa | 110 |  | 50 | 50 | 2730 | 16.67 | 150 | 150 | 0.5 | 0.013 | 0.013 | 0 | 0 | 0 | 0 | 0 | 0 | 1-2-3 are radial, tangential, axial, G12 calculated from assumed isotropy | M.Ashby 2011 Materials Selection in Mech Design (4th Ed) and K.E.Easterling 1982 On the mechanics of balsa and other woods
medium_density_foam | 130 |  | 129.2 | 129.2 | 129.2 | 48.947 | 48.947 | 48.947 | 0.32 | 0.32 | 0.32 | 4 | 4 | 4 | 3 | 3 | 3 | Airex C70.130 PVC Foam | https://www.3accorematerials.com/uploads/documents/TDS-AIREX-C70-E_1106.pdf

## Rotor Performance
Wind [m/s] | Pitch [deg] | Power [MW] | Rotor Speed [rpm] | Tip Speed [m/s] | Thrust [MN] | Torque [MNm]
3 | 0 | 0.18447 | 2.1486 | 27 | 0.18728 | 1.5241
4.1579 | 0 | 0.73982 | 2.9779 | 37.4211 | 0.35975 | 2.9276
5.3158 | 0 | 1.7019 | 3.8072 | 47.8421 | 0.58801 | 4.7853
6.4737 | 0 | 3.1712 | 4.6364 | 58.2632 | 0.87208 | 7.097
7.6316 | 0 | 5.2346 | 5.4657 | 68.6842 | 1.2119 | 9.8628
8.7895 | 0 | 7.9586 | 6.295 | 79.1053 | 1.6076 | 13.0826
9.9474 | 0 | 11.3814 | 7.1243 | 89.5263 | 2.0591 | 16.7566
10.945 | 0 | 15 | 7.5599 | 95 | 2.4171 | 21.0307
12.2632 | 5.6507 | 15 | 7.5599 | 95 | 1.7669 | 21.0307
13.4211 | 8.1686 | 15 | 7.5599 | 95 | 1.5391 | 21.0307
14.5789 | 10.2193 | 15 | 7.5599 | 95 | 1.3803 | 21.0307
15.7368 | 12.0134 | 15 | 7.5599 | 95 | 1.2595 | 21.0307
16.8947 | 13.6398 | 15 | 7.5599 | 95 | 1.1635 | 21.0307
18.0526 | 15.146 | 15 | 7.5599 | 95 | 1.0849 | 21.0307
19.2105 | 16.5604 | 15 | 7.5599 | 95 | 1.0193 | 21.0307
20.3684 | 17.9019 | 15 | 7.5599 | 95 | 0.96371 | 21.0307
21.5263 | 19.1834 | 15 | 7.5599 | 95 | 0.91604 | 21.0307
22.6842 | 20.4146 | 15 | 7.5599 | 95 | 0.87479 | 21.0307
23.8421 | 21.6024 | 15 | 7.5599 | 95 | 0.83884 | 21.0307
25 | 22.7524 | 15 | 7.5599 | 95 | 0.80731 | 21.0307

## Nacelle Mass Properties
| X_TT [m] | Z_TT [m] | Mass [kg] | I_xx [kg.m^2] | I_yy [kg.m^2] | I_zz [kg.m^2] | I_xx_shaft [kg.m^2] | I_yy_shaft [kg.m^2] | I_zz_shaft [kg.m^2]
Name
Yaw system | 0 | -0.19 | 100000 | 490266 | 490266 | 978125 | 495596 | 510794 | 952266
Turret nose | 5.786 | 4.956 | 11394 | 12571 | 10890 | 10909 | 12590 | 10890 | 10909
Inner generator stator | 5.545 | 4.913 | 226629 | 3777313 | 2012788 | 2042312 | 797126 | 2006921 | 2028366
Outer generator rotor | 6.544 | 5.033 | 144963 | 3173003 | 1673269 | 1691864 | 3189510 | 1674045 | 1674581
Shaft | 6.208 | 5 | 15734 | 33009 | 22906 | 23018 | 33120 | 22906 | 22906
Hub | 10.604 | 5.462 | 190000 | 1382171 | 2169261 | 2160637 | 1373471 | 2169282 | 2169316
Bedplate | 0.812 | 2.697 | 70329 | 398973 | 515880 | 535055 | 380821 | 517531 | 551557
Flange | 4.593 | 4.831 | 3946 | 4081 | 2065 | 2087 | 4104 | 2065 | 2065
Misc. Equipment | 0 | 0.5 | 50000 | 16667 | 16667 | 25000 | 16758 | 17017 | 24558
TDO Shaft Bearing | 6.582 | 5.04 | 2230 | 3515 | 1784 | 1803 | 3535 | 1784 | 1784
SRB Shaft Bearing | 5.388 | 4.914 | 5664 | 8930 | 4593 | 4641 | 8977 | 4593 | 4593
Nacelle total | 5.486 | 3.978 | 820888 | 12607277 | 21433958 | 18682468 | 11603661 | 21352830 | 19767213
Nacelle total minus hub | 3.945 | 3.352 | 630888 | 10680747 | 122447810 | 10046187 | 10011379 | 12173784 | 10786480