## Overview
Parameter | IEA 15 MW Reference Wind Turbine
Power rating [MW] | 15
Turbine class | IEC Class IB
Rotor diameter [m] | 242.2378
Specific rating [W/m^2] | 325.4751
Rotor orientation | Upwind
Number of blades | 3
Control | Variable speed, Collective pitch
Cut-in wind speed [m/s] | 3
Rated wind speed [m/s] | 10.6585
Cut-out wind speed [m/s] | 25
Airfoil series | FFA-W3
Hub height [m] | 150
Hub diameter [m] | 7.94
Hub Overhang [m] | -12.0313
Drive train | Low speed, Direct drive
Design tip speed ratio | 9
Minimum rotor speed [rpm] | 5
Maximum rotor speed [rpm] | 7.56
Maximum tip speed [m/s] | 95
Shaft tilt angle [deg] | 6
Rotor cone angle [deg] | 4
Tower top to hub flange height [m] | 5.614
Generator rated efficiency [%] | 0.95756
Blade pre-bend [m] | -4
Blade mass [t] | 68.3205
Hub mass [t] | 21.4049
Generator mass [t] | 368.8394
Nacelle mass [t] | 673.6502
RNA mass [t] | 947.7243
Tower mass [t] | 853.4632
Tower base diameter [m] | 10
Transition piece height [m] | 15
Monopile embedment depth [m] | 45
Monopile base diameter [m] | 10
Monopile mass [t] | 1319.2391
Volturn-S hull mass [t] | 4014.2276
Volturn-S fixed ballast mass [t] | 2540
Volturn-S fluid ballast mass [t] | 8445.0161
Volturn-S displacement [m^3] | 17755.49
Volturn-S freeboard [m] | 15
Volturn-S draft [m] | 20

## Blade Geometry
Spanwise position [r/R] | Airfoil name
0 | circular
0.02 | circular
0.15 | SNL-FFA-W3-500
0.24517 | FFA-W3-360
0.32884 | FFA-W3-330blend
0.43918 | FFA-W3-301
0.53767 | FFA-W3-270blend
0.63821 | FFA-W3-241
0.77174 | FFA-W3-211
1 | FFA-W3-211
Profile
Spanwise position [r/R] | Chord [m] | Twist [rad] | Pitch axis [x/c] | Span [m] | Prebend [m] | Sweep [m]
0 | 5.2 | 0.27218 | 0.50455 | 0 | 0 | 0
0.020408 | 5.2088 | 0.27206 | 0.49002 | 2.3878 | -0.0184 | 0
0.040816 | 5.2379 | 0.26897 | 0.4727 | 4.7755 | -0.042251 | 0
0.061224 | 5.2933 | 0.2609 | 0.45401 | 7.1633 | -0.071344 | 0
0.081633 | 5.3673 | 0.24886 | 0.43465 | 9.551 | -0.10362 | 0
0.10204 | 5.4521 | 0.23382 | 0.41563 | 11.9388 | -0.13698 | 0
0.12245 | 5.54 | 0.21681 | 0.39794 | 14.3265 | -0.16948 | 0
0.14286 | 5.6218 | 0.19887 | 0.3813 | 16.7143 | -0.19851 | 0
0.16327 | 5.6925 | 0.18101 | 0.36549 | 19.102 | -0.22314 | 0
0.18367 | 5.7426 | 0.16413 | 0.35161 | 21.4898 | -0.24054 | 0
0.20408 | 5.7648 | 0.14925 | 0.34008 | 23.8776 | -0.24887 | 0
0.22449 | 5.7561 | 0.13671 | 0.33107 | 26.2653 | -0.25025 | 0
0.2449 | 5.7031 | 0.12551 | 0.3241 | 28.6531 | -0.24941 | 0
0.26531 | 5.6047 | 0.11435 | 0.31885 | 31.0408 | -0.24757 | 0
0.28571 | 5.4716 | 0.10357 | 0.31469 | 33.4286 | -0.24482 | 0
0.30612 | 5.3228 | 0.093307 | 0.31149 | 35.8163 | -0.2413 | 0
0.32653 | 5.1665 | 0.083712 | 0.30884 | 38.2041 | -0.23699 | 0
0.34694 | 5.0194 | 0.07499 | 0.30661 | 40.5918 | -0.23242 | 0
0.36735 | 4.8858 | 0.067142 | 0.30436 | 42.9796 | -0.22531 | 0
0.38776 | 4.768 | 0.060133 | 0.30188 | 45.3673 | -0.21101 | 0
0.40816 | 4.6546 | 0.053702 | 0.2992 | 47.7551 | -0.18623 | 0
0.42857 | 4.541 | 0.04771 | 0.29649 | 50.1429 | -0.14793 | 0
0.44898 | 4.4282 | 0.042101 | 0.29397 | 52.5306 | -0.098471 | 0
0.46939 | 4.317 | 0.036856 | 0.29186 | 54.9184 | -0.041115 | 0
0.4898 | 4.2079 | 0.031912 | 0.29011 | 57.3061 | 0.02234 | 0
0.5102 | 4.1016 | 0.027206 | 0.28881 | 59.6939 | 0.088842 | 0
0.53061 | 3.9987 | 0.022732 | 0.28803 | 62.0816 | 0.15892 | 0
0.55102 | 3.8994 | 0.018578 | 0.28784 | 64.4694 | 0.24074 | 0
0.57143 | 3.8032 | 0.014721 | 0.28794 | 66.8571 | 0.33664 | 0
0.59184 | 3.7094 | 0.01111 | 0.28852 | 69.2449 | 0.44694 | 0
0.61224 | 3.6171 | 0.0076276 | 0.28958 | 71.6327 | 0.56807 | 0
0.63265 | 3.5256 | 0.0041828 | 0.29111 | 74.0204 | 0.69752 | 0
0.65306 | 3.4341 | 0.00069251 | 0.29301 | 76.4082 | 0.83213 | 0
0.67347 | 3.3419 | -0.0030164 | 0.29524 | 78.7959 | 0.96997 | 0
0.69388 | 3.2487 | -0.007105 | 0.29778 | 81.1837 | 1.1091 | 0
0.71429 | 3.1561 | -0.011875 | 0.30057 | 83.5714 | 1.2551 | 0
0.73469 | 3.0646 | -0.017441 | 0.30358 | 85.9592 | 1.4104 | 0
0.7551 | 2.973 | -0.023048 | 0.3067 | 88.3469 | 1.5733 | 0
0.77551 | 2.8807 | -0.028332 | 0.30988 | 90.7347 | 1.7435 | 0
0.79592 | 2.787 | -0.032888 | 0.31301 | 93.1224 | 1.9195 | 0
0.81633 | 2.691 | -0.036412 | 0.31639 | 95.5102 | 2.1001 | 0
0.83673 | 2.592 | -0.037769 | 0.32021 | 97.898 | 2.2855 | 0
0.85714 | 2.4893 | -0.037976 | 0.32462 | 100.2857 | 2.4757 | 0
0.87755 | 2.3839 | -0.037617 | 0.32945 | 102.6735 | 2.6734 | 0
0.89796 | 2.2759 | -0.036703 | 0.33463 | 105.0612 | 2.8783 | 0
0.91837 | 2.1655 | -0.035228 | 0.34012 | 107.449 | 3.0901 | 0
0.93878 | 2.0526 | -0.033104 | 0.34606 | 109.8367 | 3.3085 | 0
0.95918 | 1.9378 | -0.030095 | 0.35272 | 112.2245 | 3.5337 | 0
0.97959 | 1.8197 | -0.026322 | 0.36009 | 114.6122 | 3.7641 | 0
0.985 | 1.7799 | -0.025185 | 0.36216 | 115.245 | 3.8261 | 0
0.99 | 1.7078 | -0.024076 | 0.36412 | 115.83 | 3.8837 | 0
0.995 | 1.4725 | -0.02291 | 0.36613 | 116.415 | 3.9417 | 0
1 | 0.5 | -0.021684 | 0.36818 | 117 | 4 | 0

## Airfoil circular
name | circular
relative_thickness | 1
aerodynamic_center | 0.5
x | y
1 | 0
0.99901 | 0.0314
0.99606 | 0.06267
0.99114 | 0.09369
0.98429 | 0.12434
0.97553 | 0.15451
0.96489 | 0.18406
0.95241 | 0.21289
0.93815 | 0.24088
0.92216 | 0.26791
0.90451 | 0.29389
0.88526 | 0.31871
0.86448 | 0.34227
0.84227 | 0.36448
0.81871 | 0.38526
0.79389 | 0.40451
0.76791 | 0.42216
0.74088 | 0.43815
0.71289 | 0.45241
0.68406 | 0.46489
0.65451 | 0.47553
0.62434 | 0.48429
0.59369 | 0.49114
0.56267 | 0.49606
0.5314 | 0.49901
0.5 | 0.5
0.4686 | 0.49901
0.43733 | 0.49606
0.40631 | 0.49114
0.37566 | 0.48429
0.34549 | 0.47553
0.31594 | 0.46489
0.28711 | 0.45241
0.25912 | 0.43815
0.23209 | 0.42216
0.20611 | 0.40451
0.18129 | 0.38526
0.15773 | 0.36448
0.13552 | 0.34227
0.11474 | 0.31871
0.09549 | 0.29389
0.07784 | 0.26791
0.06185 | 0.24088
0.04759 | 0.21289
0.03511 | 0.18406
0.02447 | 0.15451
0.01571 | 0.12434
0.00886 | 0.09369
0.00394 | 0.06267
0.00099 | 0.0314
0 | 0
0.00099 | -0.0314
0.00394 | -0.06267
0.00886 | -0.09369
0.01571 | -0.12434
0.02447 | -0.15451
0.03511 | -0.18406
0.04759 | -0.21289
0.06185 | -0.24088
0.07784 | -0.26791
0.09549 | -0.29389
0.11474 | -0.31871
0.13552 | -0.34227
0.15773 | -0.36448
0.18129 | -0.38526
0.20611 | -0.40451
0.23209 | -0.42216
0.25912 | -0.43815
0.28711 | -0.45241
0.31594 | -0.46489
0.34549 | -0.47553
0.37566 | -0.48429
0.40631 | -0.49114
0.43733 | -0.49606
0.4686 | -0.49901
0.5 | -0.5
0.5314 | -0.49901
0.56267 | -0.49606
0.59369 | -0.49114
0.62434 | -0.48429
0.65451 | -0.47553
0.68406 | -0.46489
0.71289 | -0.45241
0.74088 | -0.43815
0.76791 | -0.42216
0.79389 | -0.40451
0.81871 | -0.38526
0.84227 | -0.36448
0.86448 | -0.34227
0.88526 | -0.31871
0.90451 | -0.29389
0.92216 | -0.26791
0.93815 | -0.24088
0.95241 | -0.21289
0.96489 | -0.18406
0.97553 | -0.15451
0.98429 | -0.12434
0.99114 | -0.09369
0.99606 | -0.06267
0.99901 | -0.0314
1 | 0
Reynolds | 3000000
alpha [rad] | c_l | c_d | c_m
-3.14 | 0.0001 | 0.35 | -0.0001
3.14 | 0.0001 | 0.35 | -0.0001

## Airfoil SNL-FFA-W3-500
name | SNL-FFA-W3-500
relative_thickness | 0.5
aerodynamic_center | 0.316
x | y
1 | 0
0.99944 | 0.01087
0.99812 | 0.011745
0.99569 | 0.013341
0.9923 | 0.015549
0.98803 | 0.0183
0.98282 | 0.021606
0.97666 | 0.02544
0.96964 | 0.029739
0.96174 | 0.034482
0.95297 | 0.039649
0.94339 | 0.045193
0.93301 | 0.050916
0.92185 | 0.057083
0.90995 | 0.063581
0.89736 | 0.070427
0.88409 | 0.077347
0.87016 | 0.084671
0.85565 | 0.09218
0.84058 | 0.099901
0.82497 | 0.10757
0.80889 | 0.11534
0.79236 | 0.12314
0.77542 | 0.13106
0.75813 | 0.13881
0.7405 | 0.14656
0.72259 | 0.15414
0.70445 | 0.16162
0.68609 | 0.16908
0.66757 | 0.17622
0.64893 | 0.18309
0.63019 | 0.18987
0.6114 | 0.19625
0.5926 | 0.20235
0.57381 | 0.20832
0.55508 | 0.21376
0.53642 | 0.21903
0.51788 | 0.22393
0.49948 | 0.22836
0.48125 | 0.23243
0.46322 | 0.23603
0.44541 | 0.23923
0.42784 | 0.24207
0.41054 | 0.2444
0.39353 | 0.24633
0.37681 | 0.24781
0.36042 | 0.24908
0.34436 | 0.24962
0.32866 | 0.25
0.31332 | 0.24991
0.29835 | 0.2494
0.28377 | 0.24844
0.26957 | 0.24723
0.25577 | 0.24556
0.24238 | 0.24358
0.2294 | 0.24125
0.21682 | 0.2386
0.20466 | 0.23566
0.19291 | 0.23243
0.18157 | 0.22884
0.17066 | 0.22497
0.16015 | 0.22083
0.15006 | 0.2165
0.14035 | 0.21198
0.13107 | 0.20723
0.12216 | 0.20232
0.11366 | 0.19717
0.10554 | 0.19204
0.097791 | 0.18656
0.090429 | 0.18109
0.083416 | 0.17546
0.076774 | 0.16968
0.070469 | 0.16379
0.0645 | 0.15776
0.058882 | 0.1517
0.053568 | 0.14556
0.048576 | 0.13949
0.043898 | 0.13334
0.039495 | 0.12705
0.035395 | 0.12087
0.031576 | 0.11469
0.028006 | 0.10849
0.024716 | 0.10222
0.021681 | 0.095893
0.018863 | 0.089807
0.016295 | 0.083748
0.013966 | 0.077738
0.011818 | 0.071879
0.0098836 | 0.06601
0.0081837 | 0.060189
0.0066313 | 0.053909
0.0052485 | 0.047327
0.0040827 | 0.040149
0.00309 | 0.033726
0.002191 | 0.02591
0.0014597 | 0.020032
0.00096333 | 0.014812
0.00059878 | 0.010964
0.00028988 | 0.0051542
7.804e-05 | 0.0023778
0 | 0
7.807e-05 | -0.0067635
0.00029009 | -0.0092701
0.00059937 | -0.014853
0.00096448 | -0.019098
0.0014626 | -0.024252
0.0021966 | -0.03028
0.0030988 | -0.037492
0.0040952 | -0.043397
0.0052677 | -0.049743
0.0066584 | -0.055936
0.0082194 | -0.061913
0.0099309 | -0.067583
0.01188 | -0.073402
0.014045 | -0.079132
0.016392 | -0.084982
0.018985 | -0.090992
0.021829 | -0.096921
0.024893 | -0.10303
0.02822 | -0.10915
0.031829 | -0.11531
0.03569 | -0.12114
0.039842 | -0.12715
0.0443 | -0.1332
0.049038 | -0.13898
0.0541 | -0.14485
0.059487 | -0.15067
0.065188 | -0.15649
0.071248 | -0.16232
0.077646 | -0.16795
0.084397 | -0.17356
0.091523 | -0.17905
0.099007 | -0.18436
0.10689 | -0.18965
0.11515 | -0.19467
0.12381 | -0.19968
0.13287 | -0.20449
0.14233 | -0.20911
0.15221 | -0.21357
0.1625 | -0.2179
0.17321 | -0.2219
0.18434 | -0.22585
0.1959 | -0.22943
0.20788 | -0.23283
0.22029 | -0.23594
0.23312 | -0.23868
0.24637 | -0.24128
0.26004 | -0.24343
0.27412 | -0.24536
0.28861 | -0.24669
0.3035 | -0.24775
0.31877 | -0.24841
0.33443 | -0.2487
0.35046 | -0.24831
0.36684 | -0.24764
0.38356 | -0.24639
0.40061 | -0.24455
0.41796 | -0.24222
0.43559 | -0.23936
0.45349 | -0.23594
0.47163 | -0.23174
0.48999 | -0.22715
0.50854 | -0.22177
0.52725 | -0.21594
0.54609 | -0.20951
0.56503 | -0.20243
0.58405 | -0.19484
0.60309 | -0.18681
0.62214 | -0.17831
0.64115 | -0.16937
0.66008 | -0.16006
0.67891 | -0.15031
0.69757 | -0.14049
0.71604 | -0.13045
0.73429 | -0.12029
0.75225 | -0.1102
0.7699 | -0.10039
0.78719 | -0.090731
0.80407 | -0.081406
0.82051 | -0.072716
0.83647 | -0.064445
0.85189 | -0.056665
0.86675 | -0.04954
0.88101 | -0.042991
0.89461 | -0.037131
0.90752 | -0.031979
0.91973 | -0.027475
0.93118 | -0.023702
0.94183 | -0.020375
0.95168 | -0.017994
0.96067 | -0.01593
0.96879 | -0.014214
0.97601 | -0.012838
0.98233 | -0.011777
0.98769 | -0.010999
0.99209 | -0.010451
0.99557 | -0.010082
0.99806 | -0.0098546
0.99943 | -0.0097435
1 | 0
Reynolds | 8100000
alpha [rad] | c_l | c_d | c_m
-3.141 | 0 | 0.0844 | 0
-2.9671 | 0.4419 | 0.0844 | 0.3125
-2.7925 | 0.8837 | 0.1268 | 0.2831
-2.618 | 0.9674 | 0.2927 | 0.2632
-2.4435 | 0.7801 | 0.497 | 0.2048
-2.2689 | 0.6293 | 0.7161 | 0.1932
-2.0944 | 0.4785 | 0.9246 | 0.2008
-1.9199 | 0.3189 | 1.0985 | 0.2136
-1.7453 | 0.1553 | 1.2182 | 0.2221
-1.5708 | 0 | 1.2707 | 0.2198
-1.3963 | -0.1553 | 1.2182 | 0.196
-1.2217 | -0.3189 | 1.0985 | 0.1635
-1.0472 | -0.4784 | 0.9246 | 0.1285
-0.87266 | -0.6293 | 0.7161 | 0.0965
-0.69813 | -0.7801 | 0.497 | 0.0716
-0.5236 | -0.9674 | 0.2927 | 0.0522
-0.34907 | -1.0281 | 0.1499 | -0.0063
-0.3447 | -1.0243 | 0.1472 | -0.0089
-0.33598 | -1.0052 | 0.1447 | -0.0099
-0.33161 | -0.9971 | 0.1433 | -0.0105
-0.32725 | -1.0052 | 0.1403 | -0.011
-0.32289 | -0.9995 | 0.1386 | -0.0116
-0.31852 | -0.9908 | 0.1373 | -0.012
-0.31416 | -0.9815 | 0.136 | -0.0126
-0.30543 | -0.9764 | 0.1322 | -0.0135
-0.30107 | -0.9705 | 0.1306 | -0.0139
-0.29671 | -0.9655 | 0.129 | -0.0143
-0.29234 | -0.9662 | 0.1268 | -0.0147
-0.28798 | -0.9544 | 0.1258 | -0.0151
-0.28362 | -0.9444 | 0.1246 | -0.0155
-0.27925 | -0.9405 | 0.1229 | -0.0158
-0.27489 | -0.9433 | 0.1206 | -0.0161
-0.27053 | -0.933 | 0.1195 | -0.0164
-0.26616 | -0.9211 | 0.1185 | -0.0168
-0.25744 | -0.9158 | 0.115 | -0.0173
-0.25307 | -0.907 | 0.1138 | -0.0175
-0.24871 | -0.8959 | 0.1127 | -0.0178
-0.24435 | -0.8926 | 0.111 | -0.0181
-0.23998 | -0.8808 | 0.11 | -0.0184
-0.23562 | -0.8722 | 0.1089 | -0.0186
-0.23126 | -0.866 | 0.1075 | -0.0188
-0.22689 | -0.8626 | 0.1059 | -0.0188
-0.22253 | -0.8489 | 0.1051 | -0.0192
-0.21817 | -0.8363 | 0.1042 | -0.0194
-0.2138 | -0.8363 | 0.1023 | -0.0194
-0.20944 | -0.8271 | 0.1013 | -0.0196
-0.20508 | -0.8141 | 0.1004 | -0.0198
-0.20071 | -0.8004 | 0.0997 | -0.02
-0.19199 | -0.789 | 0.0971 | -0.0199
-0.18762 | -0.7862 | 0.0956 | -0.0196
-0.18326 | -0.7747 | 0.0948 | -0.0194
-0.1789 | -0.7701 | 0.094 | -0.0184
-0.17453 | -0.7674 | 0.0925 | -0.0183
-0.17017 | -0.7506 | 0.0917 | -0.0192
-0.16581 | -0.729 | 0.0912 | -0.0205
-0.16144 | -0.7095 | 0.0902 | -0.0224
-0.15708 | -0.6855 | 0.0895 | -0.0247
-0.15272 | -0.659 | 0.0891 | -0.0267
-0.14835 | -0.6319 | 0.0887 | -0.0287
-0.14399 | -0.6019 | 0.0879 | -0.032
-0.13963 | -0.5718 | 0.0875 | -0.0345
-0.13526 | -0.5424 | 0.0873 | -0.0367
-0.1309 | -0.5098 | 0.0868 | -0.0399
-0.12654 | -0.4767 | 0.0864 | -0.043
-0.12217 | -0.4454 | 0.0862 | -0.0453
-0.11781 | -0.4142 | 0.086 | -0.0476
-0.11345 | -0.3791 | 0.0856 | -0.051
-0.10908 | -0.346 | 0.0853 | -0.0538
-0.10472 | -0.3144 | 0.0852 | -0.056
-0.10036 | -0.2817 | 0.085 | -0.0586
-0.09599 | -0.2461 | 0.0847 | -0.0619
-0.09163 | -0.2133 | 0.0846 | -0.0644
-0.08727 | -0.1827 | 0.0845 | -0.0663
-0.0829 | -0.1494 | 0.0843 | -0.0688
-0.07854 | -0.1158 | 0.0842 | -0.0715
-0.07418 | -0.0837 | 0.084 | -0.0737
-0.06981 | -0.0529 | 0.084 | -0.0756
-0.06545 | -0.0225 | 0.0839 | -0.0774
-0.06109 | 0.0089 | 0.0838 | -0.0793
-0.05672 | 0.0392 | 0.0838 | -0.0811
-0.05236 | 0.0686 | 0.0838 | -0.0826
-0.048 | 0.0974 | 0.0838 | -0.0838
-0.04363 | 0.126 | 0.0838 | -0.0852
-0.03927 | 0.1555 | 0.0838 | -0.0867
-0.03491 | 0.1853 | 0.0838 | -0.0883
-0.03054 | 0.2146 | 0.0837 | -0.0897
-0.02618 | 0.243 | 0.0837 | -0.091
-0.02182 | 0.2713 | 0.0838 | -0.0921
-0.01745 | 0.3006 | 0.0838 | -0.0936
-0.01309 | 0.3295 | 0.0838 | -0.0949
-0.00873 | 0.3578 | 0.0838 | -0.0961
-0.00436 | 0.3857 | 0.0838 | -0.0972
0 | 0.4135 | 0.0838 | -0.0983
0.00401 | 0.4425 | 0.0839 | -0.0995
0.0082 | 0.4715 | 0.0839 | -0.1008
0.01222 | 0.5003 | 0.0839 | -0.1019
0.01641 | 0.5286 | 0.084 | -0.1029
0.02042 | 0.5567 | 0.084 | -0.104
0.02443 | 0.585 | 0.0841 | -0.105
0.02862 | 0.6135 | 0.0841 | -0.1061
0.03264 | 0.6417 | 0.0842 | -0.1072
0.03683 | 0.6697 | 0.0842 | -0.1082
0.04084 | 0.6975 | 0.0843 | -0.1091
0.04485 | 0.7251 | 0.0843 | -0.11
0.04904 | 0.7528 | 0.0844 | -0.1109
0.05306 | 0.7807 | 0.0845 | -0.1119
0.05725 | 0.8083 | 0.0846 | -0.1128
0.06126 | 0.8358 | 0.0846 | -0.1137
0.06528 | 0.8631 | 0.0847 | -0.1146
0.06946 | 0.8902 | 0.0847 | -0.1153
0.07348 | 0.9173 | 0.0848 | -0.1161
0.07767 | 0.9444 | 0.0849 | -0.117
0.08168 | 0.9713 | 0.085 | -0.1178
0.0857 | 0.9981 | 0.0851 | -0.1185
0.08988 | 1.0249 | 0.0852 | -0.1192
0.0939 | 1.0515 | 0.0853 | -0.1199
0.09809 | 1.0779 | 0.0853 | -0.1206
0.1021 | 1.1041 | 0.0854 | -0.1212
0.10612 | 1.1302 | 0.0856 | -0.1218
0.1103 | 1.156 | 0.0857 | -0.1224
0.11432 | 1.1818 | 0.0858 | -0.123
0.11851 | 1.2076 | 0.0859 | -0.1235
0.12252 | 1.2334 | 0.086 | -0.124
0.12654 | 1.2589 | 0.0861 | -0.1245
0.13073 | 1.2841 | 0.0862 | -0.125
0.13474 | 1.3088 | 0.0864 | -0.1254
0.13893 | 1.3331 | 0.0865 | -0.1257
0.14294 | 1.357 | 0.0867 | -0.1259
0.14696 | 1.381 | 0.0869 | -0.1262
0.15115 | 1.4054 | 0.087 | -0.1265
0.15516 | 1.4295 | 0.0871 | -0.1267
0.15917 | 1.4531 | 0.0873 | -0.127
0.17244 | 1.5154 | 0.0879 | -0.1265
0.1857 | 1.5749 | 0.0886 | -0.1256
0.19897 | 1.6151 | 0.0895 | -0.1214
0.21206 | 1.6443 | 0.0912 | -0.1163
0.22532 | 1.6824 | 0.093 | -0.1133
0.23859 | 1.7146 | 0.0954 | -0.1107
0.25168 | 1.7362 | 0.0989 | -0.108
0.26494 | 1.7627 | 0.1024 | -0.1063
0.27821 | 1.7706 | 0.1076 | -0.1042
0.2913 | 1.7639 | 0.1144 | -0.1025
0.30456 | 1.7604 | 0.1211 | -0.1013
0.31782 | 1.7251 | 0.131 | -0.1001
0.33109 | 1.7035 | 0.1399 | -0.0998
0.34418 | 1.6784 | 0.1492 | -0.1001
0.35744 | 1.6505 | 0.1591 | -0.1016
0.37071 | 1.6227 | 0.1691 | -0.1036
0.3838 | 1.6067 | 0.1778 | -0.1064
0.39706 | 1.5972 | 0.1858 | -0.1099
0.41033 | 1.5892 | 0.1937 | -0.1136
0.42342 | 1.5815 | 0.2014 | -0.118
0.43668 | 1.5563 | 0.2135 | -0.1249
0.44995 | 1.5272 | 0.2267 | -0.1325
0.46304 | 1.4982 | 0.2399 | -0.14
0.4763 | 1.4691 | 0.2531 | -0.1476
0.48956 | 1.4401 | 0.2663 | -0.1551
0.50283 | 1.411 | 0.2795 | -0.1627
0.51592 | 1.382 | 0.2927 | -0.1703
0.52918 | 1.3622 | 0.3078 | -0.174
0.54245 | 1.3424 | 0.323 | -0.1777
0.55554 | 1.3225 | 0.3381 | -0.1815
0.5688 | 1.3027 | 0.3532 | -0.1852
0.58207 | 1.2829 | 0.3684 | -0.1889
0.59516 | 1.2631 | 0.3835 | -0.1926
0.60842 | 1.2433 | 0.3987 | -0.1964
0.62169 | 1.2234 | 0.4138 | -0.2001
0.63495 | 1.2036 | 0.4289 | -0.2039
0.64804 | 1.1838 | 0.4441 | -0.2076
0.66131 | 1.164 | 0.4592 | -0.2113
0.67457 | 1.1442 | 0.4743 | -0.215
0.68766 | 1.1243 | 0.4895 | -0.2188
0.70092 | 1.1064 | 0.5052 | -0.2218
0.71419 | 1.0905 | 0.5214 | -0.2242
0.72728 | 1.0745 | 0.5376 | -0.2266
0.74054 | 1.0586 | 0.5538 | -0.2289
0.75381 | 1.0426 | 0.5701 | -0.2313
0.7669 | 1.0267 | 0.5863 | -0.2337
0.78016 | 1.0107 | 0.6025 | -0.2361
0.79343 | 0.9948 | 0.6188 | -0.2384
0.80669 | 0.9788 | 0.635 | -0.2408
0.81978 | 0.9628 | 0.6512 | -0.2432
0.83305 | 0.9469 | 0.6675 | -0.2455
0.84631 | 0.9309 | 0.6837 | -0.2479
0.8594 | 0.915 | 0.6999 | -0.2503
0.87266 | 0.899 | 0.7161 | -0.2527
1.0472 | 0.6836 | 0.9246 | -0.2833
1.2217 | 0.4556 | 1.0985 | -0.3156
1.3963 | 0.2219 | 1.2182 | -0.3482
1.5708 | 0 | 1.2707 | -0.3773
1.7453 | -0.1553 | 1.2182 | -0.3877
1.9199 | -0.3189 | 1.0985 | -0.3865
2.0944 | -0.4784 | 0.9246 | -0.3806
2.2689 | -0.6293 | 0.7161 | -0.3803
2.4435 | -0.7801 | 0.497 | -0.4032
2.618 | -0.9674 | 0.2927 | -0.4854
2.7925 | -0.8837 | 0.1268 | -0.5325
2.9671 | -0.4418 | 0.0844 | -0.3906
3.141 | 0 | 0.0844 | 0

## Airfoil FFA-W3-211
name | FFA-W3-211
relative_thickness | 0.211
aerodynamic_center | 0.25
x | y
1 | 0.00094
0.99944 | 0.0010306
0.99812 | 0.0012464
0.99569 | 0.001644
0.9923 | 0.0022029
0.98803 | 0.0029141
0.98282 | 0.0037895
0.97666 | 0.0048332
0.96964 | 0.0060382
0.96174 | 0.007408
0.95297 | 0.0089448
0.94339 | 0.01064
0.93301 | 0.012524
0.92185 | 0.014572
0.90995 | 0.016797
0.89736 | 0.01918
0.88409 | 0.021743
0.87016 | 0.024455
0.85565 | 0.02735
0.84058 | 0.030383
0.82497 | 0.033558
0.80889 | 0.036877
0.79236 | 0.040346
0.77542 | 0.043947
0.75813 | 0.047663
0.7405 | 0.051486
0.72259 | 0.055408
0.70445 | 0.059358
0.68609 | 0.063388
0.66757 | 0.0674
0.64893 | 0.07143
0.63019 | 0.075418
0.6114 | 0.079381
0.5926 | 0.08322
0.57381 | 0.086949
0.55508 | 0.090537
0.53642 | 0.093994
0.51788 | 0.097297
0.49948 | 0.10037
0.48125 | 0.10331
0.46322 | 0.10607
0.44541 | 0.10853
0.42784 | 0.11081
0.41054 | 0.11273
0.39353 | 0.11447
0.37681 | 0.1159
0.36042 | 0.11703
0.34436 | 0.11783
0.32866 | 0.11838
0.31332 | 0.11853
0.29835 | 0.11842
0.28377 | 0.11789
0.26957 | 0.11713
0.25577 | 0.1161
0.24238 | 0.11482
0.2294 | 0.11325
0.21682 | 0.11141
0.20466 | 0.10943
0.19291 | 0.10729
0.18157 | 0.10496
0.17066 | 0.10246
0.16015 | 0.099935
0.15006 | 0.097204
0.14035 | 0.094413
0.13107 | 0.091569
0.12216 | 0.088633
0.11366 | 0.085645
0.10554 | 0.082602
0.097791 | 0.079541
0.090429 | 0.076474
0.083416 | 0.073383
0.076774 | 0.070292
0.070469 | 0.067199
0.0645 | 0.064114
0.058882 | 0.06106
0.053568 | 0.058025
0.048576 | 0.055034
0.043898 | 0.052079
0.039495 | 0.049149
0.035395 | 0.046271
0.031576 | 0.043449
0.028006 | 0.040662
0.024716 | 0.037958
0.021681 | 0.035308
0.018863 | 0.032692
0.016295 | 0.030158
0.013966 | 0.027684
0.011818 | 0.025257
0.0098836 | 0.022918
0.0081837 | 0.020654
0.0066313 | 0.01839
0.0052485 | 0.016327
0.0040827 | 0.014336
0.00309 | 0.012279
0.002191 | 0.010002
0.0014597 | 0.0071011
0.00096333 | 0.0046218
0.00059878 | 0.0027598
0.00028988 | 0.0012629
7.804e-05 | 0.00032267
0 | 0
7.807e-05 | -0.00031745
0.00029009 | -0.0011951
0.00059937 | -0.0024997
0.00096448 | -0.0040402
0.0014626 | -0.006058
0.0021966 | -0.0086106
0.0030988 | -0.010647
0.0040952 | -0.0123
0.0052677 | -0.013889
0.0066584 | -0.015424
0.0082194 | -0.016913
0.0099309 | -0.018543
0.01188 | -0.020297
0.014045 | -0.022061
0.016392 | -0.023835
0.018985 | -0.025713
0.021829 | -0.027644
0.024893 | -0.029602
0.02822 | -0.03163
0.031829 | -0.03371
0.03569 | -0.035826
0.039842 | -0.037993
0.0443 | -0.040207
0.049038 | -0.042453
0.0541 | -0.044738
0.059487 | -0.047051
0.065188 | -0.049389
0.071248 | -0.051769
0.077646 | -0.054171
0.084397 | -0.056588
0.091523 | -0.059015
0.099007 | -0.06144
0.10689 | -0.063866
0.11515 | -0.066273
0.12381 | -0.068648
0.13287 | -0.070998
0.14233 | -0.073294
0.15221 | -0.075545
0.1625 | -0.077734
0.17321 | -0.079826
0.18434 | -0.081825
0.1959 | -0.083709
0.20788 | -0.085448
0.22029 | -0.087035
0.23312 | -0.088466
0.24637 | -0.089717
0.26004 | -0.090753
0.27412 | -0.091577
0.28861 | -0.092161
0.3035 | -0.092458
0.31877 | -0.092474
0.33443 | -0.092163
0.35046 | -0.091493
0.36684 | -0.090468
0.38356 | -0.089039
0.40061 | -0.087207
0.41796 | -0.08496
0.43559 | -0.082262
0.45349 | -0.079111
0.47163 | -0.075502
0.48999 | -0.071475
0.50854 | -0.067052
0.52725 | -0.06234
0.54609 | -0.057432
0.56503 | -0.052357
0.58405 | -0.047189
0.60309 | -0.041968
0.62214 | -0.036815
0.64115 | -0.031776
0.66008 | -0.026925
0.67891 | -0.022307
0.69757 | -0.01798
0.71604 | -0.013981
0.73429 | -0.010324
0.75225 | -0.0070375
0.7699 | -0.004116
0.78719 | -0.0015575
0.80407 | 0.00059313
0.82051 | 0.002356
0.83647 | 0.0037555
0.85189 | 0.0048154
0.86675 | 0.0055336
0.88101 | 0.005958
0.89461 | 0.0060995
0.90752 | 0.0059969
0.91973 | 0.0056572
0.93118 | 0.0051348
0.94183 | 0.0044718
0.95168 | 0.0037738
0.96067 | 0.0030995
0.96879 | 0.0024577
0.97601 | 0.0018566
0.98233 | 0.001306
0.98769 | 0.00082003
0.99209 | 0.00040675
0.99557 | 6.986e-05
0.99806 | -0.00017578
0.99943 | -0.00031253
1 | -0.00037
Reynolds | 10000000
alpha [rad] | c_l | c_d | c_m
-3.14 | 0 | 0.024641 | 0
-3.1017 | 0.054025 | 0.025338 | 0.091429
-3.0618 | 0.10805 | 0.027424 | 0.18286
-3.0219 | 0.16208 | 0.030885 | 0.27429
-2.982 | 0.2161 | 0.035699 | 0.36571
-2.9421 | 0.27013 | 0.055991 | 0.39192
-2.9022 | 0.32415 | 0.081435 | 0.37898
-2.8623 | 0.37818 | 0.11112 | 0.36605
-2.8224 | 0.4322 | 0.14485 | 0.35312
-2.7826 | 0.48623 | 0.18242 | 0.34768
-2.7427 | 0.54025 | 0.22359 | 0.36471
-2.7028 | 0.59428 | 0.2681 | 0.38175
-2.6629 | 0.6483 | 0.31566 | 0.39878
-2.623 | 0.70233 | 0.36597 | 0.41581
-2.5831 | 0.75635 | 0.41871 | 0.41955
-2.5108 | 0.73188 | 0.51941 | 0.42287
-2.4385 | 0.70655 | 0.62488 | 0.42632
-2.3662 | 0.6776 | 0.73293 | 0.43163
-2.2939 | 0.64333 | 0.8413 | 0.43694
-2.2216 | 0.60277 | 0.94773 | 0.44389
-2.1492 | 0.5555 | 1.05 | 0.45171
-2.0769 | 0.50156 | 1.146 | 0.45897
-2.0046 | 0.44131 | 1.2337 | 0.46448
-1.9323 | 0.37542 | 1.3113 | 0.46998
-1.86 | 0.30482 | 1.3771 | 0.47096
-1.7877 | 0.23063 | 1.4299 | 0.47101
-1.7154 | 0.15413 | 1.4684 | 0.46824
-1.6431 | 0.076754 | 1.492 | 0.46149
-1.5708 | 6.9389e-17 | 1.5 | 0.45474
-1.4985 | -0.076754 | 1.492 | 0.44026
-1.4262 | -0.15413 | 1.4684 | 0.42578
-1.3539 | -0.23063 | 1.4299 | 0.40821
-1.2816 | -0.30482 | 1.3771 | 0.38846
-1.2093 | -0.37542 | 1.3113 | 0.36815
-1.137 | -0.44131 | 1.2337 | 0.34519
-1.0647 | -0.50156 | 1.146 | 0.32223
-0.99234 | -0.5555 | 1.05 | 0.29864
-0.92004 | -0.60277 | 0.94773 | 0.27486
-0.84773 | -0.64333 | 0.8413 | 0.25128
-0.77542 | -0.6776 | 0.73293 | 0.2281
-0.70312 | -0.70655 | 0.62488 | 0.20491
-0.63081 | -0.73188 | 0.51941 | 0.15416
-0.55851 | -0.75635 | 0.41871 | 0.10137
-0.48869 | -0.85636 | 0.28691 | 0.06527
-0.41888 | -1.1829 | 0.1396 | 0.016474
-0.34907 | -1.236 | 0.083446 | -0.0035156
-0.31416 | -1.2254 | 0.065092 | -0.0067166
-0.27925 | -1.2048 | 0.048882 | -0.0088127
-0.24435 | -1.1833 | 0.034172 | -0.011009
-0.20944 | -1.1009 | 0.021325 | -0.022688
-0.17453 | -0.88209 | 0.013859 | -0.043967
-0.13963 | -0.62981 | 0.010754 | -0.057559
-0.10472 | -0.3767 | 0.0088158 | -0.067475
-0.069813 | -0.12177 | 0.0070218 | -0.076804
-0.034907 | 0.1281 | 0.0066305 | -0.08283
-0.017453 | 0.25192 | 0.0066436 | -0.085344
0 | 0.37535 | 0.0067006 | -0.087772
0.017453 | 0.49828 | 0.0068082 | -0.090106
0.034907 | 0.62052 | 0.0069786 | -0.092342
0.05236 | 0.742 | 0.0072031 | -0.094469
0.069813 | 0.86238 | 0.0075148 | -0.096463
0.087266 | 0.98114 | 0.0079585 | -0.09828
0.10472 | 1.0966 | 0.0087217 | -0.099773
0.12217 | 1.209 | 0.0096835 | -0.10095
0.13963 | 1.3168 | 0.01097 | -0.10163
0.15708 | 1.4221 | 0.012275 | -0.10207
0.17453 | 1.5236 | 0.013686 | -0.10213
0.19199 | 1.6199 | 0.015288 | -0.10174
0.20944 | 1.7094 | 0.017171 | -0.10087
0.22689 | 1.7868 | 0.019735 | -0.099364
0.24435 | 1.8429 | 0.023679 | -0.097199
0.2618 | 1.8531 | 0.03094 | -0.094098
0.27925 | 1.8095 | 0.043032 | -0.091439
0.31416 | 1.6603 | 0.077304 | -0.09242
0.34907 | 1.5615 | 0.11202 | -0.098707
0.41888 | 1.4333 | 0.18408 | -0.1177
0.48869 | 1.2906 | 0.27589 | -0.14566
0.55851 | 1.0805 | 0.41871 | -0.18266
0.63081 | 1.0455 | 0.51941 | -0.20913
0.70312 | 1.0094 | 0.62488 | -0.23534
0.77542 | 0.96801 | 0.73293 | -0.25784
0.84773 | 0.91904 | 0.8413 | -0.28035
0.92004 | 0.86109 | 0.94773 | -0.30163
0.99234 | 0.79357 | 1.05 | -0.32226
1.0647 | 0.71651 | 1.146 | -0.34247
1.137 | 0.63044 | 1.2337 | -0.36135
1.2093 | 0.53632 | 1.3113 | -0.38024
1.2816 | 0.43546 | 1.3771 | -0.39704
1.3539 | 0.32947 | 1.4299 | -0.41341
1.4262 | 0.22019 | 1.4684 | -0.42844
1.4985 | 0.10965 | 1.492 | -0.44159
1.5708 | 9.7145e-17 | 1.5 | -0.45474
1.6431 | -0.076754 | 1.492 | -0.46149
1.7154 | -0.15413 | 1.4684 | -0.46824
1.7877 | -0.23063 | 1.4299 | -0.47101
1.86 | -0.30482 | 1.3771 | -0.47096
1.9323 | -0.37542 | 1.3113 | -0.46998
2.0046 | -0.44131 | 1.2337 | -0.46448
2.0769 | -0.50156 | 1.146 | -0.45897
2.1492 | -0.5555 | 1.05 | -0.45171
2.2216 | -0.60277 | 0.94773 | -0.44389
2.2939 | -0.64333 | 0.8413 | -0.43694
2.3662 | -0.6776 | 0.73293 | -0.43163
2.4385 | -0.70655 | 0.62488 | -0.42632
2.5108 | -0.73188 | 0.51941 | -0.42287
2.5831 | -0.75635 | 0.41871 | -0.41955
2.623 | -0.70233 | 0.36597 | -0.41581
2.6629 | -0.6483 | 0.31566 | -0.39878
2.7028 | -0.59428 | 0.2681 | -0.38175
2.7427 | -0.54025 | 0.22359 | -0.36471
2.7826 | -0.48623 | 0.18242 | -0.34768
2.8224 | -0.4322 | 0.14485 | -0.37026
2.8623 | -0.37818 | 0.11112 | -0.40605
2.9022 | -0.32415 | 0.081435 | -0.44184
2.9421 | -0.27013 | 0.055991 | -0.47763
2.982 | -0.2161 | 0.035699 | -0.45714
3.0219 | -0.16208 | 0.030885 | -0.34286
3.0618 | -0.10805 | 0.027424 | -0.22857
3.1017 | -0.054025 | 0.025338 | -0.11429
3.14 | 4.8572e-18 | 0.024641 | 0

## Airfoil FFA-W3-241
name | FFA-W3-241
relative_thickness | 0.241
aerodynamic_center | 0.25
x | y
1 | 0.00425
0.99944 | 0.0043621
0.99812 | 0.0046283
0.99569 | 0.005117
0.9923 | 0.0057996
0.98803 | 0.0066615
0.98282 | 0.0077128
0.97666 | 0.0089541
0.96964 | 0.010373
0.96174 | 0.011969
0.95297 | 0.013742
0.94339 | 0.015682
0.93301 | 0.017786
0.92185 | 0.020069
0.90995 | 0.022517
0.89736 | 0.025138
0.88409 | 0.027909
0.87016 | 0.030849
0.85565 | 0.033936
0.84058 | 0.037164
0.82497 | 0.040529
0.80889 | 0.04401
0.79236 | 0.047617
0.77542 | 0.051327
0.75813 | 0.055123
0.7405 | 0.058994
0.72259 | 0.062934
0.70445 | 0.066901
0.68609 | 0.070883
0.66757 | 0.074867
0.64893 | 0.078835
0.63019 | 0.082754
0.6114 | 0.086614
0.5926 | 0.090373
0.57381 | 0.094025
0.55508 | 0.097549
0.53642 | 0.10093
0.51788 | 0.10415
0.49948 | 0.10719
0.48125 | 0.11006
0.46322 | 0.11271
0.44541 | 0.11515
0.42784 | 0.11735
0.41054 | 0.11932
0.39353 | 0.12103
0.37681 | 0.12249
0.36042 | 0.12368
0.34436 | 0.1246
0.32866 | 0.12524
0.31332 | 0.12561
0.29835 | 0.12567
0.28377 | 0.12547
0.26957 | 0.12499
0.25577 | 0.12424
0.24238 | 0.12324
0.2294 | 0.122
0.21682 | 0.12054
0.20466 | 0.11887
0.19291 | 0.11699
0.18157 | 0.11493
0.17066 | 0.11269
0.16015 | 0.1103
0.15006 | 0.10777
0.14035 | 0.10511
0.13107 | 0.10233
0.12216 | 0.09945
0.11366 | 0.09649
0.10554 | 0.093459
0.097791 | 0.090364
0.090429 | 0.087222
0.083416 | 0.084034
0.076774 | 0.080827
0.070469 | 0.077594
0.0645 | 0.074348
0.058882 | 0.07111
0.053568 | 0.067873
0.048576 | 0.064653
0.043898 | 0.061454
0.039495 | 0.05826
0.035395 | 0.055109
0.031576 | 0.051996
0.028006 | 0.048918
0.024716 | 0.045891
0.021681 | 0.042896
0.018863 | 0.039919
0.016295 | 0.037002
0.013966 | 0.034185
0.011818 | 0.031372
0.0098836 | 0.028611
0.0081837 | 0.026038
0.0066313 | 0.023429
0.0052485 | 0.020761
0.0040827 | 0.018305
0.00309 | 0.015951
0.002191 | 0.013271
0.0014597 | 0.010499
0.00096333 | 0.0074621
0.00059878 | 0.0045372
0.00028988 | 0.0020445
7.804e-05 | 0.00050657
0 | 0
7.807e-05 | -0.00049018
0.00029009 | -0.0018413
0.00059937 | -0.0038182
0.00096448 | -0.0060571
0.0014626 | -0.0087056
0.0021966 | -0.011229
0.0030988 | -0.013422
0.0040952 | -0.015344
0.0052677 | -0.017167
0.0066584 | -0.019096
0.0082194 | -0.021307
0.0099309 | -0.023514
0.01188 | -0.025799
0.014045 | -0.02816
0.016392 | -0.03054
0.018985 | -0.032969
0.021829 | -0.035491
0.024893 | -0.038075
0.02822 | -0.040726
0.031829 | -0.04346
0.03569 | -0.046232
0.039842 | -0.04907
0.0443 | -0.05197
0.049038 | -0.054909
0.0541 | -0.057904
0.059487 | -0.06095
0.065188 | -0.064025
0.071248 | -0.067128
0.077646 | -0.070244
0.084397 | -0.07337
0.091523 | -0.076491
0.099007 | -0.079596
0.10689 | -0.082683
0.11515 | -0.085719
0.12381 | -0.088705
0.13287 | -0.091617
0.14233 | -0.094438
0.15221 | -0.097166
0.1625 | -0.09977
0.17321 | -0.10224
0.18434 | -0.10454
0.1959 | -0.10669
0.20788 | -0.10863
0.22029 | -0.11037
0.23312 | -0.11188
0.24637 | -0.11314
0.26004 | -0.11415
0.27412 | -0.11487
0.28861 | -0.1153
0.3035 | -0.11538
0.31877 | -0.11513
0.33443 | -0.11451
0.35046 | -0.1135
0.36684 | -0.11208
0.38356 | -0.11023
0.40061 | -0.10793
0.41796 | -0.10519
0.43559 | -0.10198
0.45349 | -0.098298
0.47163 | -0.094141
0.48999 | -0.089522
0.50854 | -0.084473
0.52725 | -0.079057
0.54609 | -0.07331
0.56503 | -0.0673
0.58405 | -0.061093
0.60309 | -0.054771
0.62214 | -0.048425
0.64115 | -0.042138
0.66008 | -0.036008
0.67891 | -0.030127
0.69757 | -0.024575
0.71604 | -0.019421
0.73429 | -0.014701
0.75225 | -0.010454
0.7699 | -0.0067345
0.78719 | -0.0035584
0.80407 | -0.00093374
0.82051 | 0.0011792
0.83647 | 0.002846
0.85189 | 0.0040941
0.86675 | 0.0049525
0.88101 | 0.0054653
0.89461 | 0.0056196
0.90752 | 0.0054773
0.91973 | 0.0050471
0.93118 | 0.004404
0.94183 | 0.0036087
0.95168 | 0.0027081
0.96067 | 0.0018027
0.96879 | 0.00091285
0.97601 | 5.718e-05
0.98233 | -0.00074311
0.98769 | -0.0014613
0.99209 | -0.0020799
0.99557 | -0.0025891
0.99806 | -0.0029629
0.99943 | -0.003172
1 | -0.00326
Reynolds | 10000000
alpha [rad] | c_l | c_d | c_m
-3.14 | 0 | 0.011775 | 0
-3.1017 | 0.058178 | 0.012482 | 0.091429
-3.0618 | 0.11636 | 0.014599 | 0.18286
-3.0219 | 0.17453 | 0.018111 | 0.27429
-2.982 | 0.23271 | 0.022996 | 0.36571
-2.9421 | 0.29089 | 0.029224 | 0.39568
-2.9022 | 0.34907 | 0.05382 | 0.38876
-2.8623 | 0.40725 | 0.083794 | 0.38184
-2.8224 | 0.46542 | 0.11786 | 0.37492
-2.7826 | 0.5236 | 0.15581 | 0.37408
-2.7427 | 0.58178 | 0.1974 | 0.39148
-2.7028 | 0.63996 | 0.24237 | 0.40888
-2.6629 | 0.69814 | 0.29043 | 0.42628
-2.623 | 0.75631 | 0.34128 | 0.44368
-2.5831 | 0.81449 | 0.3946 | 0.44537
-2.5108 | 0.77925 | 0.49645 | 0.44436
-2.4385 | 0.74511 | 0.60319 | 0.4436
-2.3662 | 0.70881 | 0.71263 | 0.44609
-2.2939 | 0.66835 | 0.82249 | 0.44858
-2.2216 | 0.62253 | 0.93051 | 0.4537
-2.1492 | 0.5708 | 1.0345 | 0.4602
-2.0769 | 0.51307 | 1.1322 | 0.46633
-2.0046 | 0.44965 | 1.2218 | 0.4713
-1.9323 | 0.38115 | 1.3012 | 0.47627
-1.86 | 0.30846 | 1.369 | 0.47705
-1.7877 | 0.23266 | 1.4238 | 0.47695
-1.7154 | 0.15503 | 1.4643 | 0.47409
-1.6431 | 0.076979 | 1.4899 | 0.46732
-1.5708 | 6.9389e-17 | 1.5 | 0.46055
-1.4985 | -0.076979 | 1.4899 | 0.44509
-1.4262 | -0.15503 | 1.4643 | 0.42964
-1.3539 | -0.23266 | 1.4238 | 0.41125
-1.2816 | -0.30846 | 1.369 | 0.39081
-1.2093 | -0.38115 | 1.3012 | 0.36988
-1.137 | -0.44965 | 1.2218 | 0.34663
-1.0647 | -0.51307 | 1.1322 | 0.32339
-0.99234 | -0.5708 | 1.0345 | 0.29984
-0.92004 | -0.62253 | 0.93051 | 0.27618
-0.84773 | -0.66835 | 0.82249 | 0.2528
-0.77542 | -0.70881 | 0.71263 | 0.22992
-0.70312 | -0.74511 | 0.60319 | 0.20705
-0.63081 | -0.77925 | 0.49645 | 0.14561
-0.55851 | -0.81449 | 0.3946 | 0.081308
-0.48869 | -1.0778 | 0.22252 | 0.045917
-0.41888 | -1.1269 | 0.15159 | 0.01901
-0.34907 | -1.1448 | 0.096988 | 0.00063155
-0.31416 | -1.128 | 0.077435 | -0.0034225
-0.27925 | -1.0939 | 0.061222 | -0.0058652
-0.24435 | -1.0596 | 0.046672 | -0.0065213
-0.20944 | -1.0312 | 0.033022 | -0.0075541
-0.17453 | -0.93706 | 0.020269 | -0.022432
-0.13963 | -0.6738 | 0.011679 | -0.055829
-0.10472 | -0.40391 | 0.0091782 | -0.07159
-0.069813 | -0.14226 | 0.0083876 | -0.081225
-0.034907 | 0.1158 | 0.008105 | -0.08892
-0.017453 | 0.24382 | 0.0080825 | -0.092353
0 | 0.37113 | 0.0081278 | -0.095564
0.017453 | 0.49766 | 0.0082403 | -0.098568
0.034907 | 0.62334 | 0.0084182 | -0.10139
0.05236 | 0.74798 | 0.0086734 | -0.10403
0.069813 | 0.87137 | 0.0090086 | -0.10645
0.087266 | 0.9932 | 0.0094473 | -0.10863
0.10472 | 1.1133 | 0.0099783 | -0.11057
0.12217 | 1.2304 | 0.010702 | -0.11214
0.13963 | 1.345 | 0.011528 | -0.11337
0.15708 | 1.4541 | 0.012694 | -0.11396
0.17453 | 1.5591 | 0.013965 | -0.11403
0.19199 | 1.6578 | 0.015453 | -0.11336
0.20944 | 1.7483 | 0.017243 | -0.11187
0.22689 | 1.8267 | 0.019611 | -0.10935
0.24435 | 1.8883 | 0.022932 | -0.10606
0.2618 | 1.9258 | 0.027953 | -0.10238
0.27925 | 1.9272 | 0.036091 | -0.098869
0.31416 | 1.8006 | 0.065343 | -0.09497
0.34907 | 1.6309 | 0.10459 | -0.099957
0.41888 | 1.4334 | 0.19148 | -0.12589
0.48869 | 1.288 | 0.28629 | -0.15453
0.55851 | 1.1636 | 0.3946 | -0.18396
0.63081 | 1.1132 | 0.49645 | -0.21099
0.70312 | 1.0644 | 0.60319 | -0.23768
0.77542 | 1.0126 | 0.71263 | -0.25992
0.84773 | 0.95478 | 0.82249 | -0.28216
0.92004 | 0.88932 | 0.93051 | -0.30323
0.99234 | 0.81542 | 1.0345 | -0.32368
1.0647 | 0.73296 | 1.1322 | -0.3438
1.137 | 0.64236 | 1.2218 | -0.36292
1.2093 | 0.5445 | 1.3012 | -0.38204
1.2816 | 0.44065 | 1.369 | -0.39944
1.3539 | 0.33237 | 1.4238 | -0.41648
1.4262 | 0.22148 | 1.4643 | -0.43231
1.4985 | 0.10997 | 1.4899 | -0.44643
1.5708 | 9.7145e-17 | 1.5 | -0.46055
1.6431 | -0.076979 | 1.4899 | -0.46732
1.7154 | -0.15503 | 1.4643 | -0.47409
1.7877 | -0.23266 | 1.4238 | -0.47695
1.86 | -0.30846 | 1.369 | -0.47705
1.9323 | -0.38115 | 1.3012 | -0.47627
2.0046 | -0.44965 | 1.2218 | -0.4713
2.0769 | -0.51307 | 1.1322 | -0.46633
2.1492 | -0.5708 | 1.0345 | -0.4602
2.2216 | -0.62253 | 0.93051 | -0.4537
2.2939 | -0.66835 | 0.82249 | -0.44858
2.3662 | -0.70881 | 0.71263 | -0.44609
2.4385 | -0.74511 | 0.60319 | -0.4436
2.5108 | -0.77925 | 0.49645 | -0.44436
2.5831 | -0.81449 | 0.3946 | -0.44537
2.623 | -0.75631 | 0.34128 | -0.44368
2.6629 | -0.69814 | 0.29043 | -0.42628
2.7028 | -0.63996 | 0.24237 | -0.40888
2.7427 | -0.58178 | 0.1974 | -0.39148
2.7826 | -0.5236 | 0.15581 | -0.37408
2.8224 | -0.46542 | 0.11786 | -0.39207
2.8623 | -0.40725 | 0.083794 | -0.42184
2.9022 | -0.34907 | 0.05382 | -0.45162
2.9421 | -0.29089 | 0.029224 | -0.48139
2.982 | -0.23271 | 0.022996 | -0.45714
3.0219 | -0.17453 | 0.018111 | -0.34286
3.0618 | -0.11636 | 0.014599 | -0.22857
3.1017 | -0.058178 | 0.012482 | -0.11429
3.14 | 0 | 0.011775 | 0

## Airfoil FFA-W3-270blend
name | FFA-W3-270blend
relative_thickness | 0.27
aerodynamic_center | 0.25
x | y
1 | 0.00652
0.99185 | 0.00831
0.98371 | 0.0101
0.97556 | 0.01188
0.96742 | 0.01366
0.95928 | 0.01544
0.95114 | 0.01721
0.94301 | 0.01898
0.93488 | 0.02076
0.92675 | 0.02255
0.91863 | 0.02435
0.91052 | 0.02617
0.90241 | 0.02799
0.8943 | 0.02982
0.8862 | 0.03166
0.8781 | 0.0335
0.87001 | 0.03535
0.86192 | 0.03721
0.85384 | 0.03907
0.84576 | 0.04094
0.83768 | 0.04281
0.8296 | 0.04468
0.82153 | 0.04655
0.81346 | 0.04843
0.80539 | 0.05031
0.79732 | 0.05219
0.78926 | 0.05407
0.7812 | 0.05594
0.77314 | 0.05782
0.76508 | 0.05969
0.75702 | 0.06157
0.74897 | 0.06343
0.74091 | 0.0653
0.73285 | 0.06716
0.7248 | 0.06901
0.71675 | 0.07086
0.70869 | 0.0727
0.70064 | 0.07453
0.69258 | 0.07636
0.68452 | 0.07817
0.67647 | 0.07997
0.66841 | 0.08176
0.66035 | 0.08355
0.65229 | 0.08531
0.64422 | 0.08707
0.63616 | 0.08881
0.62809 | 0.09054
0.62002 | 0.09225
0.61195 | 0.09395
0.60387 | 0.09562
0.5958 | 0.09729
0.58772 | 0.09893
0.57963 | 0.10055
0.57154 | 0.10215
0.56345 | 0.10373
0.55536 | 0.10529
0.54726 | 0.10683
0.53916 | 0.10834
0.53105 | 0.10983
0.52294 | 0.11129
0.51482 | 0.11272
0.5067 | 0.11413
0.49858 | 0.11551
0.49045 | 0.11686
0.48231 | 0.11817
0.47417 | 0.11946
0.46603 | 0.1207
0.45787 | 0.12191
0.44972 | 0.12307
0.44155 | 0.1242
0.43338 | 0.12529
0.42521 | 0.12633
0.41702 | 0.12733
0.40884 | 0.12828
0.40064 | 0.12918
0.39244 | 0.13003
0.38424 | 0.13083
0.37602 | 0.13157
0.36781 | 0.13226
0.35958 | 0.13288
0.35135 | 0.13345
0.34312 | 0.13395
0.33488 | 0.13438
0.32664 | 0.13474
0.31839 | 0.13502
0.31014 | 0.13523
0.30188 | 0.13537
0.29363 | 0.13541
0.28537 | 0.13537
0.27711 | 0.13524
0.26886 | 0.13501
0.2606 | 0.13469
0.25235 | 0.13426
0.24411 | 0.13373
0.23587 | 0.13308
0.22763 | 0.13233
0.21941 | 0.13146
0.2112 | 0.13048
0.20301 | 0.12936
0.19483 | 0.12811
0.18668 | 0.12672
0.17855 | 0.12518
0.17045 | 0.1235
0.16238 | 0.12167
0.15434 | 0.11969
0.14635 | 0.11754
0.1384 | 0.11522
0.1305 | 0.11274
0.12265 | 0.11008
0.11487 | 0.10724
0.10716 | 0.10422
0.09952 | 0.10101
0.09197 | 0.09759
0.08451 | 0.09398
0.07715 | 0.09014
0.06991 | 0.08609
0.0628 | 0.0818
0.05584 | 0.07727
0.04905 | 0.07247
0.04245 | 0.06739
0.03607 | 0.06196
0.02994 | 0.05624
0.02413 | 0.05049
0.01869 | 0.04439
0.0137 | 0.03792
0.00923 | 0.03107
0.0054 | 0.02383
0.00249 | 0.01614
0.00064 | 0.00809
0 | -0.00019
0.00089 | -0.00845
0.00355 | -0.01641
0.00749 | -0.02407
0.01224 | -0.03122
0.01762 | -0.03781
0.0234 | -0.04403
0.02952 | -0.0499
0.03592 | -0.05547
0.04253 | -0.06076
0.04932 | -0.06581
0.05615 | -0.07063
0.06309 | -0.07523
0.07018 | -0.07962
0.0774 | -0.08382
0.08474 | -0.08782
0.09218 | -0.09164
0.09973 | -0.09527
0.10736 | -0.09873
0.11507 | -0.10201
0.12286 | -0.10512
0.13073 | -0.10805
0.13866 | -0.11082
0.14664 | -0.11341
0.15469 | -0.11584
0.16279 | -0.11811
0.17093 | -0.12022
0.17911 | -0.12218
0.18733 | -0.12397
0.19559 | -0.12562
0.20387 | -0.12711
0.21219 | -0.12846
0.22053 | -0.12966
0.22889 | -0.13073
0.23726 | -0.13166
0.24566 | -0.13245
0.25406 | -0.13312
0.26248 | -0.13365
0.2709 | -0.13406
0.27933 | -0.13435
0.28777 | -0.13451
0.2962 | -0.13455
0.30464 | -0.13447
0.31308 | -0.13428
0.32151 | -0.13397
0.32994 | -0.13354
0.33836 | -0.13301
0.34678 | -0.13236
0.35518 | -0.13161
0.36358 | -0.13075
0.37196 | -0.12978
0.38033 | -0.12871
0.38869 | -0.12753
0.39703 | -0.12626
0.40536 | -0.12489
0.41366 | -0.12341
0.42195 | -0.12185
0.43023 | -0.1202
0.43848 | -0.11845
0.44671 | -0.11662
0.45493 | -0.1147
0.46312 | -0.1127
0.47129 | -0.11061
0.47944 | -0.10845
0.48757 | -0.10621
0.49567 | -0.1039
0.50376 | -0.10152
0.51182 | -0.09907
0.51986 | -0.09656
0.52788 | -0.09399
0.53589 | -0.09137
0.54387 | -0.0887
0.55184 | -0.08599
0.55979 | -0.08323
0.56773 | -0.08044
0.57566 | -0.07761
0.58358 | -0.07476
0.59149 | -0.07188
0.59939 | -0.06898
0.60729 | -0.06607
0.61518 | -0.06315
0.62308 | -0.06024
0.63098 | -0.05732
0.63888 | -0.05441
0.64679 | -0.05152
0.65471 | -0.04864
0.66263 | -0.04579
0.67057 | -0.04297
0.67853 | -0.04019
0.68649 | -0.03745
0.69448 | -0.03476
0.70248 | -0.03213
0.7105 | -0.02955
0.71854 | -0.02704
0.7266 | -0.02459
0.73468 | -0.02222
0.74278 | -0.01993
0.75091 | -0.01771
0.75905 | -0.01559
0.76722 | -0.01356
0.77541 | -0.01163
0.78362 | -0.00982
0.79186 | -0.00814
0.80012 | -0.00656
0.80839 | -0.00511
0.81669 | -0.00377
0.82499 | -0.00254
0.83332 | -0.00143
0.84165 | -0.00044
0.85 | 0.00045
0.85835 | 0.00121
0.86671 | 0.00185
0.87508 | 0.00237
0.88346 | 0.00275
0.89184 | 0.003
0.90022 | 0.0031
0.90859 | 0.00305
0.91697 | 0.00287
0.92533 | 0.00254
0.93369 | 0.00207
0.94203 | 0.00147
0.95037 | 0.00074
0.95868 | -0.00012
0.96698 | -0.00112
0.97526 | -0.00224
0.98352 | -0.00347
0.99177 | -0.00479
1 | -0.00613
Reynolds | 10000000
alpha [rad] | c_l | c_d | c_m
-3.14 | 0 | 0.015451 | 0
-3.1017 | 0.062129 | 0.016108 | 0.091429
-3.0618 | 0.12426 | 0.018073 | 0.18286
-3.0219 | 0.18639 | 0.021333 | 0.27429
-2.982 | 0.24852 | 0.025868 | 0.36571
-2.9421 | 0.31064 | 0.032888 | 0.39874
-2.9022 | 0.37277 | 0.056807 | 0.39672
-2.8623 | 0.4349 | 0.084714 | 0.3947
-2.8224 | 0.49703 | 0.11643 | 0.39268
-2.7826 | 0.55916 | 0.15176 | 0.39544
-2.7427 | 0.62129 | 0.19048 | 0.41254
-2.7028 | 0.68342 | 0.23234 | 0.42964
-2.6629 | 0.74555 | 0.27708 | 0.44674
-2.623 | 0.80768 | 0.32441 | 0.46384
-2.5831 | 0.86981 | 0.37404 | 0.46186
-2.5108 | 0.8166 | 0.46882 | 0.45335
-2.4385 | 0.76812 | 0.56814 | 0.44523
-2.3662 | 0.7204 | 0.66995 | 0.44237
-2.2939 | 0.67095 | 0.77214 | 0.43951
-2.2216 | 0.61828 | 0.87258 | 0.44072
-2.1492 | 0.56158 | 0.96921 | 0.44407
-2.0769 | 0.50057 | 1.06 | 0.44739
-2.0046 | 0.4354 | 1.1432 | 0.45063
-1.9323 | 0.36655 | 1.2169 | 0.45387
-1.86 | 0.29475 | 1.2797 | 0.45377
-1.7877 | 0.22098 | 1.3303 | 0.45298
-1.7154 | 0.14639 | 1.3677 | 0.44973
-1.6431 | 0.072269 | 1.3911 | 0.44302
-1.5708 | 5.5511e-17 | 1.4 | 0.4363
-1.4985 | -0.072269 | 1.3911 | 0.4218
-1.4262 | -0.14639 | 1.3677 | 0.4073
-1.3539 | -0.22098 | 1.3303 | 0.3902
-1.2816 | -0.29475 | 1.2797 | 0.37125
-1.2093 | -0.36655 | 1.2169 | 0.3519
-1.137 | -0.4354 | 1.1432 | 0.33068
-1.0647 | -0.50057 | 1.06 | 0.30945
-0.99234 | -0.56158 | 0.96921 | 0.28815
-0.92004 | -0.61828 | 0.87258 | 0.26684
-0.84773 | -0.67095 | 0.77214 | 0.24576
-0.77542 | -0.7204 | 0.66995 | 0.22512
-0.70312 | -0.76812 | 0.56814 | 0.20447
-0.63081 | -0.8166 | 0.46882 | 0.13957
-0.55851 | -0.86981 | 0.37404 | 0.071382
-0.48869 | -1.0984 | 0.2188 | 0.043998
-0.41888 | -1.0834 | 0.15982 | 0.02166
-0.34907 | -1.0699 | 0.10744 | 0.0042194
-0.31416 | -1.0545 | 0.086904 | -0.00035185
-0.27925 | -1.0343 | 0.068443 | -0.0033372
-0.24435 | -1.0836 | 0.047334 | -0.0028317
-0.20944 | -1.0949 | 0.030849 | -0.0055562
-0.17453 | -0.92665 | 0.019843 | -0.029517
-0.13963 | -0.69676 | 0.014394 | -0.048218
-0.10472 | -0.43628 | 0.011549 | -0.064832
-0.069813 | -0.16252 | 0.010264 | -0.079187
-0.034907 | 0.10709 | 0.0097551 | -0.090407
-0.017453 | 0.23993 | 0.0096708 | -0.095173
0 | 0.37158 | 0.0096775 | -0.099533
0.017453 | 0.5021 | 0.0097641 | -0.10355
0.034907 | 0.63139 | 0.0099289 | -0.10725
0.05236 | 0.75951 | 0.010161 | -0.11068
0.069813 | 0.88638 | 0.010454 | -0.11385
0.087266 | 1.0117 | 0.010823 | -0.11673
0.10472 | 1.1343 | 0.011399 | -0.11923
0.12217 | 1.2554 | 0.011979 | -0.12145
0.13963 | 1.3738 | 0.012669 | -0.12328
0.15708 | 1.4884 | 0.01353 | -0.1246
0.17453 | 1.5978 | 0.014604 | -0.12526
0.19199 | 1.7001 | 0.015967 | -0.12505
0.20944 | 1.7919 | 0.017767 | -0.1237
0.22689 | 1.8678 | 0.02035 | -0.12093
0.24435 | 1.9269 | 0.02385 | -0.11725
0.2618 | 1.909 | 0.032357 | -0.10931
0.27925 | 1.8855 | 0.042586 | -0.10525
0.31416 | 1.7211 | 0.076715 | -0.10292
0.34907 | 1.5474 | 0.11914 | -0.11017
0.41888 | 1.3718 | 0.20189 | -0.13431
0.48869 | 1.3361 | 0.27981 | -0.15777
0.55851 | 1.2426 | 0.37404 | -0.18432
0.63081 | 1.1666 | 0.46882 | -0.21002
0.70312 | 1.0973 | 0.56814 | -0.23531
0.77542 | 1.0291 | 0.66995 | -0.25508
0.84773 | 0.9585 | 0.77214 | -0.27485
0.92004 | 0.88325 | 0.87258 | -0.29346
0.99234 | 0.80225 | 0.96921 | -0.31145
1.0647 | 0.7151 | 1.06 | -0.32925
1.137 | 0.622 | 1.1432 | -0.34641
1.2093 | 0.52364 | 1.2169 | -0.36357
1.2816 | 0.42107 | 1.2797 | -0.37949
1.3539 | 0.31569 | 1.3303 | -0.39517
1.4262 | 0.20913 | 1.3677 | -0.40983
1.4985 | 0.10324 | 1.3911 | -0.42306
1.5708 | 8.3267e-17 | 1.4 | -0.4363
1.6431 | -0.072269 | 1.3911 | -0.44302
1.7154 | -0.14639 | 1.3677 | -0.44973
1.7877 | -0.22098 | 1.3303 | -0.45298
1.86 | -0.29475 | 1.2797 | -0.45377
1.9323 | -0.36655 | 1.2169 | -0.45387
2.0046 | -0.4354 | 1.1432 | -0.45063
2.0769 | -0.50057 | 1.06 | -0.44739
2.1492 | -0.56158 | 0.96921 | -0.44407
2.2216 | -0.61828 | 0.87258 | -0.44072
2.2939 | -0.67095 | 0.77214 | -0.43951
2.3662 | -0.7204 | 0.66995 | -0.44237
2.4385 | -0.76812 | 0.56814 | -0.44523
2.5108 | -0.8166 | 0.46882 | -0.45335
2.5831 | -0.86981 | 0.37404 | -0.46186
2.623 | -0.80768 | 0.32441 | -0.46384
2.6629 | -0.74555 | 0.27708 | -0.44674
2.7028 | -0.68342 | 0.23234 | -0.42964
2.7427 | -0.62129 | 0.19048 | -0.41254
2.7826 | -0.55916 | 0.15176 | -0.39544
2.8224 | -0.49703 | 0.11643 | -0.40982
2.8623 | -0.4349 | 0.084714 | -0.4347
2.9022 | -0.37277 | 0.056807 | -0.45958
2.9421 | -0.31064 | 0.032888 | -0.48445
2.982 | -0.24852 | 0.025868 | -0.45714
3.0219 | -0.18639 | 0.021333 | -0.34286
3.0618 | -0.12426 | 0.018073 | -0.22857
3.1017 | -0.062129 | 0.016108 | -0.11429
3.14 | 0 | 0.015451 | 0

## Airfoil FFA-W3-301
name | FFA-W3-301
relative_thickness | 0.301
aerodynamic_center | 0.25
x | y
1 | 0.0091
0.99944 | 0.0092
0.99812 | 0.0095
0.99569 | 0.010191
0.9923 | 0.010987
0.98803 | 0.011993
0.98282 | 0.01322
0.97666 | 0.014669
0.96964 | 0.016325
0.96174 | 0.018189
0.95297 | 0.020262
0.94339 | 0.022529
0.93301 | 0.024989
0.92185 | 0.027656
0.90995 | 0.030536
0.89736 | 0.033613
0.88409 | 0.036882
0.87016 | 0.040328
0.85565 | 0.043942
0.84058 | 0.047719
0.82497 | 0.051634
0.80889 | 0.055681
0.79236 | 0.059826
0.77542 | 0.064066
0.75813 | 0.068384
0.7405 | 0.072757
0.72259 | 0.077169
0.70445 | 0.081593
0.68609 | 0.086
0.66757 | 0.090393
0.64893 | 0.094736
0.63019 | 0.099018
0.6114 | 0.10323
0.5926 | 0.10734
0.57381 | 0.11135
0.55508 | 0.11524
0.53642 | 0.11897
0.51788 | 0.12256
0.49948 | 0.126
0.48125 | 0.12923
0.46322 | 0.13226
0.44541 | 0.13506
0.42784 | 0.13763
0.41054 | 0.13995
0.39353 | 0.14203
0.37681 | 0.14383
0.36042 | 0.14537
0.34436 | 0.14664
0.32866 | 0.14763
0.31332 | 0.14835
0.29835 | 0.14878
0.28377 | 0.14892
0.26957 | 0.14878
0.25577 | 0.14835
0.24238 | 0.14764
0.2294 | 0.14666
0.21682 | 0.14541
0.20466 | 0.14389
0.19291 | 0.14212
0.18157 | 0.1401
0.17066 | 0.13784
0.16015 | 0.13536
0.15006 | 0.13268
0.14035 | 0.12981
0.13107 | 0.12676
0.12216 | 0.12357
0.11366 | 0.12023
0.10554 | 0.11677
0.097791 | 0.11319
0.090429 | 0.10953
0.083416 | 0.10579
0.076774 | 0.10198
0.070469 | 0.098121
0.0645 | 0.094223
0.058882 | 0.090316
0.053568 | 0.086375
0.048576 | 0.082428
0.043898 | 0.078495
0.039495 | 0.074555
0.035395 | 0.070655
0.031576 | 0.066783
0.028006 | 0.062927
0.024716 | 0.059123
0.021681 | 0.055364
0.018863 | 0.051615
0.016295 | 0.047935
0.013966 | 0.044343
0.011818 | 0.040736
0.0098836 | 0.03723
0.0081837 | 0.033847
0.0066313 | 0.030417
0.0052485 | 0.027079
0.0040827 | 0.023859
0.00309 | 0.020692
0.002191 | 0.017626
0.0014597 | 0.014402
0.00096333 | 0.011485
0.00059878 | 0.0081594
0.00028988 | 0.0039343
7.804e-05 | 0.0009904
0 | 0
7.807e-05 | -0.00098225
0.00029009 | -0.0038427
0.00059937 | -0.0079089
0.00096448 | -0.011194
0.0014626 | -0.013959
0.0021966 | -0.017027
0.0030988 | -0.019863
0.0040952 | -0.022777
0.0052677 | -0.025854
0.0066584 | -0.029027
0.0082194 | -0.032254
0.0099309 | -0.035475
0.01188 | -0.038798
0.014045 | -0.042224
0.016392 | -0.045662
0.018985 | -0.049187
0.021829 | -0.052812
0.024893 | -0.056457
0.02822 | -0.060182
0.031829 | -0.063977
0.03569 | -0.067814
0.039842 | -0.071712
0.0443 | -0.075671
0.049038 | -0.079648
0.0541 | -0.083659
0.059487 | -0.087691
0.065188 | -0.091728
0.071248 | -0.095775
0.077646 | -0.0998
0.084397 | -0.1038
0.091523 | -0.10777
0.099007 | -0.11167
0.10689 | -0.11551
0.11515 | -0.11925
0.12381 | -0.12288
0.13287 | -0.1264
0.14233 | -0.12976
0.15221 | -0.13296
0.1625 | -0.13598
0.17321 | -0.1388
0.18434 | -0.14139
0.1959 | -0.14375
0.20788 | -0.14585
0.22029 | -0.14768
0.23312 | -0.14922
0.24637 | -0.15044
0.26004 | -0.15134
0.27412 | -0.1519
0.28861 | -0.15208
0.3035 | -0.15188
0.31877 | -0.15128
0.33443 | -0.15027
0.35046 | -0.14881
0.36684 | -0.1469
0.38356 | -0.14451
0.40061 | -0.14165
0.41796 | -0.13829
0.43559 | -0.13444
0.45349 | -0.1301
0.47163 | -0.12526
0.48999 | -0.11993
0.50854 | -0.11414
0.52725 | -0.10792
0.54609 | -0.10132
0.56503 | -0.09438
0.58405 | -0.08718
0.60309 | -0.079795
0.62214 | -0.072304
0.64115 | -0.064818
0.66008 | -0.057433
0.67891 | -0.050235
0.69757 | -0.043331
0.71604 | -0.036803
0.73429 | -0.03072
0.75225 | -0.025123
0.7699 | -0.020046
0.78719 | -0.01556
0.80407 | -0.0117
0.82051 | -0.0084086
0.83647 | -0.0056702
0.85189 | -0.0034675
0.86675 | -0.0017734
0.88101 | -0.00057044
0.89461 | 0.00016442
0.90752 | 0.00045227
0.91973 | 0.00040686
0.93118 | 4.808e-05
0.94183 | -0.00057005
0.95168 | -0.0014277
0.96067 | -0.0024128
0.96879 | -0.00347
0.97601 | -0.0045494
0.98233 | -0.0056022
0.98769 | -0.0065754
0.99209 | -0.0074312
0.99557 | -0.008146
0.99806 | -0.008676
0.99943 | -0.0089741
1 | -0.0091
Reynolds | 10000000
alpha [rad] | c_l | c_d | c_m
-3.14 | 0 | 0.02454 | 0
-3.1017 | 0.065082 | 0.025141 | 0.091429
-3.0618 | 0.13016 | 0.026941 | 0.18286
-3.0219 | 0.19525 | 0.029929 | 0.27429
-2.982 | 0.26033 | 0.034084 | 0.36571
-2.9421 | 0.32541 | 0.039379 | 0.40085
-2.9022 | 0.39049 | 0.059103 | 0.4022
-2.8623 | 0.45557 | 0.084949 | 0.40356
-2.8224 | 0.52066 | 0.11433 | 0.40492
-2.7826 | 0.58574 | 0.14704 | 0.4101
-2.7427 | 0.65082 | 0.1829 | 0.42678
-2.7028 | 0.7159 | 0.22166 | 0.44345
-2.6629 | 0.78098 | 0.26309 | 0.46013
-2.623 | 0.84607 | 0.30692 | 0.4768
-2.5831 | 0.91115 | 0.35287 | 0.47162
-2.5108 | 0.84257 | 0.44061 | 0.45656
-2.4385 | 0.78187 | 0.53255 | 0.44202
-2.3662 | 0.72448 | 0.62677 | 0.43452
-2.2939 | 0.66755 | 0.72131 | 0.42701
-2.2216 | 0.60928 | 0.81421 | 0.42483
-2.1492 | 0.54868 | 0.90355 | 0.42544
-2.0769 | 0.4853 | 0.98748 | 0.42634
-2.0046 | 0.41915 | 1.0642 | 0.42813
-1.9323 | 0.35056 | 1.1323 | 0.42992
-1.86 | 0.28017 | 1.1902 | 0.42916
-1.7877 | 0.20881 | 1.2367 | 0.42788
-1.7154 | 0.13754 | 1.2709 | 0.42444
-1.6431 | 0.067506 | 1.2922 | 0.41794
-1.5708 | 5.5511e-17 | 1.3 | 0.41144
-1.4985 | -0.067506 | 1.2922 | 0.39804
-1.4262 | -0.13754 | 1.2709 | 0.38464
-1.3539 | -0.20881 | 1.2367 | 0.36892
-1.2816 | -0.28017 | 1.1902 | 0.35157
-1.2093 | -0.35056 | 1.1323 | 0.33391
-1.137 | -0.41915 | 1.0642 | 0.31474
-1.0647 | -0.4853 | 0.98748 | 0.29557
-0.99234 | -0.54868 | 0.90355 | 0.27653
-0.92004 | -0.60928 | 0.81421 | 0.25754
-0.84773 | -0.66755 | 0.72131 | 0.23873
-0.77542 | -0.72448 | 0.62677 | 0.22027
-0.70312 | -0.78187 | 0.53255 | 0.20181
-0.63081 | -0.84257 | 0.44061 | 0.13644
-0.55851 | -0.91115 | 0.35287 | 0.067597
-0.48869 | -1.1035 | 0.21721 | 0.042306
-0.41888 | -1.1074 | 0.15629 | 0.020255
-0.34907 | -1.1182 | 0.10335 | 0.0040659
-0.31416 | -1.1233 | 0.081804 | 0.0001727
-0.27925 | -1.1187 | 0.063307 | -0.0016692
-0.24435 | -1.1162 | 0.047183 | -0.0011956
-0.20944 | -1.0959 | 0.032802 | -0.004634
-0.17453 | -0.91767 | 0.023515 | -0.024936
-0.13963 | -0.69311 | 0.017929 | -0.043039
-0.10472 | -0.45396 | 0.014306 | -0.058675
-0.069813 | -0.17779 | 0.012423 | -0.076012
-0.034907 | 0.1048 | 0.011595 | -0.091212
-0.017453 | 0.24383 | 0.01143 | -0.097633
0 | 0.38111 | 0.011381 | -0.10341
0.017453 | 0.5166 | 0.011432 | -0.10861
0.034907 | 0.65044 | 0.011564 | -0.11333
0.05236 | 0.78267 | 0.011767 | -0.11762
0.069813 | 0.91326 | 0.012042 | -0.12154
0.087266 | 1.0421 | 0.012393 | -0.1251
0.10472 | 1.1687 | 0.012834 | -0.12828
0.12217 | 1.293 | 0.013379 | -0.13104
0.13963 | 1.4139 | 0.014059 | -0.13332
0.15708 | 1.5309 | 0.014882 | -0.13503
0.17453 | 1.6421 | 0.015919 | -0.13599
0.19199 | 1.7457 | 0.017257 | -0.13605
0.20944 | 1.8389 | 0.019079 | -0.13514
0.22689 | 1.9176 | 0.021687 | -0.13322
0.24435 | 1.9741 | 0.02572 | -0.1302
0.2618 | 1.9992 | 0.03222 | -0.12641
0.27925 | 1.9938 | 0.041569 | -0.12265
0.31416 | 1.9172 | 0.067308 | -0.11675
0.34907 | 1.7368 | 0.10526 | -0.11652
0.41888 | 1.4732 | 0.19229 | -0.1379
0.48869 | 1.3602 | 0.27449 | -0.16242
0.55851 | 1.3016 | 0.35287 | -0.18463
0.63081 | 1.2037 | 0.44061 | -0.20894
0.70312 | 1.117 | 0.53255 | -0.23276
0.77542 | 1.035 | 0.62677 | -0.25011
0.84773 | 0.95364 | 0.72131 | -0.26746
0.92004 | 0.8704 | 0.81421 | -0.28365
0.99234 | 0.78383 | 0.90355 | -0.29923
1.0647 | 0.69329 | 0.98748 | -0.31472
1.137 | 0.59878 | 1.0642 | -0.32988
1.2093 | 0.5008 | 1.1323 | -0.34505
1.2816 | 0.40024 | 1.1902 | -0.35942
1.3539 | 0.29831 | 1.2367 | -0.37363
1.4262 | 0.19648 | 1.2709 | -0.38702
1.4985 | 0.096437 | 1.2922 | -0.39923
1.5708 | 8.3267e-17 | 1.3 | -0.41144
1.6431 | -0.067506 | 1.2922 | -0.41794
1.7154 | -0.13754 | 1.2709 | -0.42444
1.7877 | -0.20881 | 1.2367 | -0.42788
1.86 | -0.28017 | 1.1902 | -0.42916
1.9323 | -0.35056 | 1.1323 | -0.42992
2.0046 | -0.41915 | 1.0642 | -0.42813
2.0769 | -0.4853 | 0.98748 | -0.42634
2.1492 | -0.54868 | 0.90355 | -0.42544
2.2216 | -0.60928 | 0.81421 | -0.42483
2.2939 | -0.66755 | 0.72131 | -0.42701
2.3662 | -0.72448 | 0.62677 | -0.43452
2.4385 | -0.78187 | 0.53255 | -0.44202
2.5108 | -0.84257 | 0.44061 | -0.45656
2.5831 | -0.91115 | 0.35287 | -0.47162
2.623 | -0.84607 | 0.30692 | -0.4768
2.6629 | -0.78098 | 0.26309 | -0.46013
2.7028 | -0.7159 | 0.22166 | -0.44345
2.7427 | -0.65082 | 0.1829 | -0.42678
2.7826 | -0.58574 | 0.14704 | -0.4101
2.8224 | -0.52066 | 0.11433 | -0.42206
2.8623 | -0.45557 | 0.084949 | -0.44356
2.9022 | -0.39049 | 0.059103 | -0.46506
2.9421 | -0.32541 | 0.039379 | -0.48656
2.982 | -0.26033 | 0.034084 | -0.45714
3.0219 | -0.19525 | 0.029929 | -0.34286
3.0618 | -0.13016 | 0.026941 | -0.22857
3.1017 | -0.065082 | 0.025141 | -0.11429
3.14 | 0 | 0.02454 | 0

## Airfoil FFA-W3-330blend
name | FFA-W3-330blend
relative_thickness | 0.33
aerodynamic_center | 0.25
x | y
1 | 0.01245
0.9917 | 0.0146
0.98339 | 0.01675
0.97509 | 0.01888
0.96678 | 0.021
0.95847 | 0.0231
0.95016 | 0.0252
0.94186 | 0.0273
0.93356 | 0.0294
0.92526 | 0.03151
0.91697 | 0.03364
0.90869 | 0.03578
0.90042 | 0.03793
0.89215 | 0.04009
0.88388 | 0.04226
0.87562 | 0.04443
0.86736 | 0.0466
0.85911 | 0.04878
0.85086 | 0.05097
0.84261 | 0.05315
0.83437 | 0.05535
0.82613 | 0.05754
0.81789 | 0.05973
0.80966 | 0.06193
0.80143 | 0.06412
0.7932 | 0.0663
0.78497 | 0.06849
0.77674 | 0.07067
0.76852 | 0.07285
0.76029 | 0.07503
0.75207 | 0.0772
0.74385 | 0.07937
0.73562 | 0.08153
0.7274 | 0.08369
0.71918 | 0.08584
0.71096 | 0.08798
0.70273 | 0.09011
0.69451 | 0.09223
0.68629 | 0.09434
0.67806 | 0.09644
0.66983 | 0.09853
0.66161 | 0.10062
0.65338 | 0.10268
0.64514 | 0.10474
0.63691 | 0.10678
0.62867 | 0.10881
0.62044 | 0.11083
0.61219 | 0.11283
0.60395 | 0.11481
0.5957 | 0.11678
0.58745 | 0.11874
0.5792 | 0.12067
0.57094 | 0.12259
0.56268 | 0.12449
0.55441 | 0.12636
0.54614 | 0.12822
0.53787 | 0.13005
0.52959 | 0.13187
0.5213 | 0.13365
0.51301 | 0.13542
0.50471 | 0.13715
0.49641 | 0.13886
0.48813 | 0.14053
0.47986 | 0.14218
0.47159 | 0.14378
0.4633 | 0.14536
0.45501 | 0.14689
0.44671 | 0.14838
0.4384 | 0.14984
0.43008 | 0.15124
0.42176 | 0.1526
0.41342 | 0.15392
0.40507 | 0.15518
0.39672 | 0.15639
0.38835 | 0.15755
0.37998 | 0.15865
0.37159 | 0.15969
0.3632 | 0.16067
0.35479 | 0.16158
0.34638 | 0.16242
0.33796 | 0.16319
0.32953 | 0.16389
0.32109 | 0.16451
0.31264 | 0.16504
0.30418 | 0.16549
0.29572 | 0.16586
0.28725 | 0.16613
0.27878 | 0.1663
0.2703 | 0.16636
0.26182 | 0.16632
0.25334 | 0.16615
0.24486 | 0.16587
0.23638 | 0.16546
0.2279 | 0.16491
0.21943 | 0.16423
0.21097 | 0.1634
0.20253 | 0.1624
0.1941 | 0.16125
0.1857 | 0.15991
0.17733 | 0.15839
0.16898 | 0.15668
0.16068 | 0.15478
0.15243 | 0.15266
0.14423 | 0.15033
0.1361 | 0.14779
0.12803 | 0.14502
0.12004 | 0.14203
0.11215 | 0.1388
0.10436 | 0.13531
0.09669 | 0.13157
0.08915 | 0.12757
0.08176 | 0.12331
0.07453 | 0.11877
0.06748 | 0.11395
0.06064 | 0.10886
0.05402 | 0.10348
0.04763 | 0.09783
0.04151 | 0.09189
0.03567 | 0.08568
0.03015 | 0.07919
0.02498 | 0.07242
0.02018 | 0.06539
0.01577 | 0.0581
0.01178 | 0.05056
0.0083 | 0.04277
0.00551 | 0.03473
0.0034 | 0.02648
0.00177 | 0.01806
0.00052 | 0.00955
0 | 0.00098
0.00048 | -0.00761
0.00174 | -0.01613
0.00344 | -0.02443
0.00581 | -0.03254
0.00892 | -0.04061
0.01269 | -0.0484
0.01696 | -0.05589
0.02165 | -0.0631
0.02674 | -0.07004
0.03223 | -0.07669
0.03808 | -0.08304
0.04424 | -0.0891
0.05068 | -0.09487
0.05737 | -0.10036
0.06428 | -0.10559
0.07139 | -0.11054
0.07869 | -0.11522
0.08616 | -0.11964
0.09378 | -0.1238
0.10153 | -0.12771
0.1094 | -0.13138
0.11738 | -0.13483
0.12545 | -0.13805
0.13361 | -0.14107
0.14184 | -0.14388
0.15013 | -0.14648
0.15849 | -0.14889
0.16691 | -0.15111
0.17537 | -0.15313
0.18388 | -0.15498
0.19242 | -0.15666
0.20099 | -0.15816
0.2096 | -0.1595
0.21822 | -0.16068
0.22687 | -0.16169
0.23554 | -0.16255
0.24423 | -0.16325
0.25292 | -0.16381
0.26162 | -0.16421
0.27033 | -0.16447
0.27905 | -0.16458
0.28776 | -0.16456
0.29648 | -0.1644
0.30519 | -0.1641
0.31389 | -0.16368
0.32259 | -0.16312
0.33128 | -0.16244
0.33996 | -0.16164
0.34863 | -0.16071
0.35728 | -0.15967
0.36592 | -0.15851
0.37455 | -0.15723
0.38315 | -0.15585
0.39174 | -0.15435
0.40031 | -0.15274
0.40885 | -0.15103
0.41738 | -0.14921
0.42588 | -0.14729
0.43435 | -0.14527
0.44281 | -0.14316
0.45123 | -0.14094
0.45963 | -0.13864
0.46801 | -0.13625
0.47636 | -0.13378
0.48469 | -0.13123
0.493 | -0.12861
0.50128 | -0.12592
0.50954 | -0.12316
0.51777 | -0.12034
0.52599 | -0.11746
0.53418 | -0.11452
0.54235 | -0.11153
0.5505 | -0.10849
0.55863 | -0.1054
0.56675 | -0.10226
0.57484 | -0.09909
0.58293 | -0.09589
0.591 | -0.09265
0.59905 | -0.08939
0.6071 | -0.08611
0.61517 | -0.08281
0.62324 | -0.0795
0.63131 | -0.07618
0.63937 | -0.07286
0.64743 | -0.06955
0.65549 | -0.06624
0.66356 | -0.06295
0.67163 | -0.05968
0.67971 | -0.05644
0.6878 | -0.05323
0.6959 | -0.05005
0.70402 | -0.04693
0.71216 | -0.04386
0.72031 | -0.04085
0.72849 | -0.0379
0.73669 | -0.03502
0.74491 | -0.03221
0.75315 | -0.02949
0.76143 | -0.02685
0.76973 | -0.02431
0.77805 | -0.02187
0.78641 | -0.01954
0.7948 | -0.01733
0.80321 | -0.01523
0.81165 | -0.01325
0.82012 | -0.01138
0.82861 | -0.00965
0.83712 | -0.00805
0.84566 | -0.00658
0.85422 | -0.00526
0.8628 | -0.0041
0.87141 | -0.0031
0.88003 | -0.00227
0.88866 | -0.00161
0.89733 | -0.00114
0.90601 | -0.00084
0.91468 | -0.00073
0.92334 | -0.00081
0.93199 | -0.00107
0.94063 | -0.00152
0.94925 | -0.00216
0.95784 | -0.00302
0.96639 | -0.00415
0.97489 | -0.00559
0.98332 | -0.00734
0.99168 | -0.00939
1 | -0.01163
Reynolds | 10000000
alpha [rad] | c_l | c_d | c_m
-3.14 | 0 | 0.031686 | 0
-3.1017 | 0.069601 | 0.032281 | 0.091429
-3.0618 | 0.1392 | 0.034065 | 0.18286
-3.0219 | 0.2088 | 0.037024 | 0.27429
-2.982 | 0.27841 | 0.041139 | 0.36571
-2.9421 | 0.34801 | 0.046383 | 0.40308
-2.9022 | 0.41761 | 0.05732 | 0.40801
-2.8623 | 0.48721 | 0.083186 | 0.41294
-2.8224 | 0.55681 | 0.11258 | 0.41788
-2.7826 | 0.62641 | 0.14533 | 0.42586
-2.7427 | 0.69601 | 0.18121 | 0.44302
-2.7028 | 0.76562 | 0.22 | 0.46017
-2.6629 | 0.83522 | 0.26146 | 0.47732
-2.623 | 0.90482 | 0.30532 | 0.49447
-2.5831 | 0.97442 | 0.35131 | 0.48743
-2.5108 | 0.89412 | 0.43913 | 0.46839
-2.4385 | 0.82382 | 0.53115 | 0.44996
-2.3662 | 0.75845 | 0.62546 | 0.43985
-2.2939 | 0.69477 | 0.7201 | 0.42974
-2.2216 | 0.63079 | 0.8131 | 0.42589
-2.1492 | 0.56532 | 0.90255 | 0.42535
-2.0769 | 0.49783 | 0.98659 | 0.42528
-2.0046 | 0.42823 | 1.0635 | 0.42673
-1.9323 | 0.3568 | 1.1316 | 0.42817
-1.86 | 0.28412 | 1.1896 | 0.42745
-1.7877 | 0.21103 | 1.2363 | 0.42628
-1.7154 | 0.13851 | 1.2707 | 0.42303
-1.6431 | 0.06775 | 1.292 | 0.41683
-1.5708 | 5.5511e-17 | 1.3 | 0.41063
-1.4985 | -0.06775 | 1.292 | 0.39752
-1.4262 | -0.13851 | 1.2707 | 0.38441
-1.3539 | -0.21103 | 1.2363 | 0.36905
-1.2816 | -0.28412 | 1.1896 | 0.35212
-1.2093 | -0.3568 | 1.1316 | 0.33491
-1.137 | -0.42823 | 1.0635 | 0.31634
-1.0647 | -0.49783 | 0.98659 | 0.29777
-0.99234 | -0.56532 | 0.90255 | 0.27947
-0.92004 | -0.63079 | 0.8131 | 0.26125
-0.84773 | -0.69477 | 0.7201 | 0.24322
-0.77542 | -0.75845 | 0.62546 | 0.22556
-0.70312 | -0.82382 | 0.53115 | 0.20789
-0.63081 | -0.89412 | 0.43913 | 0.13731
-0.55851 | -0.97442 | 0.35131 | 0.062799
-0.48869 | -1.1631 | 0.20648 | 0.039049
-0.41888 | -1.1489 | 0.15001 | 0.01853
-0.34907 | -1.0945 | 0.106 | 0.0044075
-0.31416 | -1.058 | 0.087319 | -0.00060625
-0.27925 | -1.0228 | 0.07051 | -0.0034157
-0.24435 | -0.9981 | 0.054741 | -0.0040144
-0.20944 | -0.98515 | 0.040516 | -0.0027205
-0.17453 | -0.89583 | 0.02929 | -0.011979
-0.13963 | -0.67539 | 0.022067 | -0.034578
-0.10472 | -0.43247 | 0.017352 | -0.054656
-0.069813 | -0.15881 | 0.014727 | -0.074255
-0.034907 | 0.13456 | 0.013624 | -0.092697
-0.017453 | 0.28014 | 0.013391 | -0.10074
0 | 0.42386 | 0.013299 | -0.10802
0.017453 | 0.56519 | 0.013325 | -0.1145
0.034907 | 0.7041 | 0.01345 | -0.12028
0.05236 | 0.84071 | 0.013665 | -0.12546
0.069813 | 0.975 | 0.01397 | -0.13011
0.087266 | 1.1068 | 0.014369 | -0.13425
0.10472 | 1.236 | 0.014862 | -0.13793
0.12217 | 1.3622 | 0.015472 | -0.14108
0.13963 | 1.4842 | 0.016227 | -0.14363
0.15708 | 1.601 | 0.017176 | -0.14545
0.17453 | 1.7101 | 0.018408 | -0.14636
0.19199 | 1.8096 | 0.020096 | -0.14635
0.20944 | 1.8947 | 0.02258 | -0.14544
0.22689 | 1.957 | 0.026709 | -0.14378
0.24435 | 1.9858 | 0.033802 | -0.14185
0.2618 | 1.9926 | 0.043331 | -0.14004
0.27925 | 1.9962 | 0.053544 | -0.13823
0.31416 | 1.964 | 0.07706 | -0.13351
0.34907 | 1.8118 | 0.11169 | -0.13135
0.41888 | 1.5607 | 0.19103 | -0.1466
0.48869 | 1.468 | 0.27199 | -0.17242
0.55851 | 1.392 | 0.35131 | -0.19417
0.63081 | 1.2773 | 0.43913 | -0.21792
0.70312 | 1.1769 | 0.53115 | -0.24115
0.77542 | 1.0835 | 0.62546 | -0.25734
0.84773 | 0.99253 | 0.7201 | -0.27354
0.92004 | 0.90112 | 0.8131 | -0.28862
0.99234 | 0.8076 | 0.90255 | -0.30311
1.0647 | 0.71119 | 0.98659 | -0.31757
1.137 | 0.61175 | 1.0635 | -0.33194
1.2093 | 0.50971 | 1.1316 | -0.34631
1.2816 | 0.40589 | 1.1896 | -0.36014
1.3539 | 0.30146 | 1.2363 | -0.37385
1.4262 | 0.19788 | 1.2707 | -0.38681
1.4985 | 0.096786 | 1.292 | -0.39872
1.5708 | 8.3267e-17 | 1.3 | -0.41063
1.6431 | -0.06775 | 1.292 | -0.41683
1.7154 | -0.13851 | 1.2707 | -0.42303
1.7877 | -0.21103 | 1.2363 | -0.42628
1.86 | -0.28412 | 1.1896 | -0.42745
1.9323 | -0.3568 | 1.1316 | -0.42817
2.0046 | -0.42823 | 1.0635 | -0.42673
2.0769 | -0.49783 | 0.98659 | -0.42528
2.1492 | -0.56532 | 0.90255 | -0.42535
2.2216 | -0.63079 | 0.8131 | -0.42589
2.2939 | -0.69477 | 0.7201 | -0.42974
2.3662 | -0.75845 | 0.62546 | -0.43985
2.4385 | -0.82382 | 0.53115 | -0.44996
2.5108 | -0.89412 | 0.43913 | -0.46839
2.5831 | -0.97442 | 0.35131 | -0.48743
2.623 | -0.90482 | 0.30532 | -0.49447
2.6629 | -0.83522 | 0.26146 | -0.47732
2.7028 | -0.76562 | 0.22 | -0.46017
2.7427 | -0.69601 | 0.18121 | -0.44302
2.7826 | -0.62641 | 0.14533 | -0.42586
2.8224 | -0.55681 | 0.11258 | -0.43502
2.8623 | -0.48721 | 0.083186 | -0.45294
2.9022 | -0.41761 | 0.05732 | -0.47087
2.9421 | -0.34801 | 0.046383 | -0.4888
2.982 | -0.27841 | 0.041139 | -0.45714
3.0219 | -0.2088 | 0.037024 | -0.34286
3.0618 | -0.1392 | 0.034065 | -0.22857
3.1017 | -0.069601 | 0.032281 | -0.11429
3.14 | 0 | 0.031686 | 0

## Airfoil FFA-W3-360
name | FFA-W3-360
relative_thickness | 0.36
aerodynamic_center | 0.25
x | y
1 | 0.01298
0.99944 | 0.013259
0.99812 | 0.013537
0.99569 | 0.014255
0.9923 | 0.015254
0.98803 | 0.016511
0.98282 | 0.018037
0.97666 | 0.019828
0.96964 | 0.021864
0.96174 | 0.024141
0.95297 | 0.026657
0.94339 | 0.029394
0.93301 | 0.032321
0.92185 | 0.035461
0.90995 | 0.038828
0.89736 | 0.042419
0.88409 | 0.046219
0.87016 | 0.050211
0.85565 | 0.054375
0.84058 | 0.058712
0.82497 | 0.063204
0.80889 | 0.067832
0.79236 | 0.072584
0.77542 | 0.077445
0.75813 | 0.08239
0.7405 | 0.087405
0.72259 | 0.092487
0.70445 | 0.097591
0.68609 | 0.10272
0.66757 | 0.10785
0.64893 | 0.11295
0.63019 | 0.11803
0.6114 | 0.12305
0.5926 | 0.12799
0.57381 | 0.13283
0.55508 | 0.13755
0.53642 | 0.14213
0.51788 | 0.14656
0.49948 | 0.1508
0.48125 | 0.15483
0.46322 | 0.15865
0.44541 | 0.16221
0.42784 | 0.16553
0.41054 | 0.16856
0.39353 | 0.17132
0.37681 | 0.17376
0.36042 | 0.17591
0.34436 | 0.17774
0.32866 | 0.17926
0.31332 | 0.18046
0.29835 | 0.18133
0.28377 | 0.18188
0.26957 | 0.18211
0.25577 | 0.18204
0.24238 | 0.18164
0.2294 | 0.18094
0.21682 | 0.17993
0.20466 | 0.17862
0.19291 | 0.17702
0.18157 | 0.17511
0.17066 | 0.17293
0.16015 | 0.17049
0.15006 | 0.16779
0.14035 | 0.16485
0.13107 | 0.16169
0.12216 | 0.15833
0.11366 | 0.15479
0.10554 | 0.15108
0.097791 | 0.14721
0.090429 | 0.14319
0.083416 | 0.13901
0.076774 | 0.13472
0.070469 | 0.13032
0.0645 | 0.12582
0.058882 | 0.12122
0.053568 | 0.11653
0.048576 | 0.11179
0.043898 | 0.107
0.039495 | 0.10215
0.035395 | 0.097293
0.031576 | 0.092423
0.028006 | 0.087512
0.024716 | 0.082622
0.021681 | 0.077746
0.018863 | 0.072823
0.016295 | 0.06793
0.013966 | 0.063145
0.011818 | 0.058394
0.0098836 | 0.053712
0.0081837 | 0.049301
0.0066313 | 0.044623
0.0052485 | 0.039552
0.0040827 | 0.034234
0.00309 | 0.028127
0.002191 | 0.021599
0.0014597 | 0.01656
0.00096333 | 0.012525
0.00059878 | 0.0086197
0.00028988 | 0.0043303
7.804e-05 | 0.0011648
0 | 0
7.807e-05 | -0.0012214
0.00029009 | -0.0049302
0.00059937 | -0.010066
0.00096448 | -0.014042
0.0014626 | -0.018185
0.0021966 | -0.02326
0.0030988 | -0.028951
0.0040952 | -0.034027
0.0052677 | -0.038674
0.0066584 | -0.04323
0.0082194 | -0.047687
0.0099309 | -0.051948
0.01188 | -0.0564
0.014045 | -0.060956
0.016392 | -0.065501
0.018985 | -0.070153
0.021829 | -0.074836
0.024893 | -0.07944
0.02822 | -0.084032
0.031829 | -0.088619
0.03569 | -0.093153
0.039842 | -0.097677
0.0443 | -0.1022
0.049038 | -0.10668
0.0541 | -0.11114
0.059487 | -0.11555
0.065188 | -0.11989
0.071248 | -0.12417
0.077646 | -0.12835
0.084397 | -0.13245
0.091523 | -0.13644
0.099007 | -0.14033
0.10689 | -0.14411
0.11515 | -0.14776
0.12381 | -0.1513
0.13287 | -0.1547
0.14233 | -0.15793
0.15221 | -0.16099
0.1625 | -0.16386
0.17321 | -0.16653
0.18434 | -0.16899
0.1959 | -0.17121
0.20788 | -0.17318
0.22029 | -0.17489
0.23312 | -0.1763
0.24637 | -0.17738
0.26004 | -0.17813
0.27412 | -0.1785
0.28861 | -0.17852
0.3035 | -0.17811
0.31877 | -0.17729
0.33443 | -0.17604
0.35046 | -0.17434
0.36684 | -0.17216
0.38356 | -0.1695
0.40061 | -0.16633
0.41796 | -0.16264
0.43559 | -0.1584
0.45349 | -0.15362
0.47163 | -0.14833
0.48999 | -0.14257
0.50854 | -0.13636
0.52725 | -0.12974
0.54609 | -0.12273
0.56503 | -0.11537
0.58405 | -0.10772
0.60309 | -0.099844
0.62214 | -0.091786
0.64115 | -0.083648
0.66008 | -0.075518
0.67891 | -0.067495
0.69757 | -0.05968
0.71604 | -0.052192
0.73429 | -0.045098
0.75225 | -0.038499
0.7699 | -0.03246
0.78719 | -0.027003
0.80407 | -0.022133
0.82051 | -0.017863
0.83647 | -0.014198
0.85189 | -0.011163
0.86675 | -0.0087689
0.88101 | -0.0069716
0.89461 | -0.0057485
0.90752 | -0.0050322
0.91973 | -0.0047916
0.93118 | -0.004
0.94183 | -0.0037
0.95168 | -0.0034
0.96067 | -0.0031
0.96879 | -0.0028
0.97601 | -0.0025
0.98233 | -0.0022
0.98769 | -0.0019
0.99209 | -0.0016
0.99557 | -0.0013
0.99806 | -0.001
0.99943 | -0.001
1 | -0.001
Reynolds | 10000000
alpha [rad] | c_l | c_d | c_m
-3.14 | 0 | 0.037148 | 0
-3.1017 | 0.071781 | 0.037739 | 0.091429
-3.0618 | 0.14356 | 0.039509 | 0.18286
-3.0219 | 0.21534 | 0.042446 | 0.27429
-2.982 | 0.28713 | 0.046531 | 0.36571
-2.9421 | 0.35891 | 0.051737 | 0.40313
-2.9022 | 0.43069 | 0.060678 | 0.40814
-2.8623 | 0.50247 | 0.086508 | 0.41315
-2.8224 | 0.57425 | 0.11586 | 0.41816
-2.7826 | 0.64603 | 0.14856 | 0.42627
-2.7427 | 0.71781 | 0.18439 | 0.4437
-2.7028 | 0.7896 | 0.22313 | 0.46114
-2.6629 | 0.86138 | 0.26453 | 0.47857
-2.623 | 0.93316 | 0.30832 | 0.496
-2.5831 | 1.0049 | 0.35424 | 0.4883
-2.5108 | 0.91898 | 0.44192 | 0.46784
-2.4385 | 0.84406 | 0.53379 | 0.44803
-2.3662 | 0.77483 | 0.62793 | 0.43697
-2.2939 | 0.7079 | 0.72238 | 0.42591
-2.2216 | 0.64116 | 0.8152 | 0.4215
-2.1492 | 0.57335 | 0.90444 | 0.42058
-2.0769 | 0.50388 | 0.98826 | 0.42024
-2.0046 | 0.43261 | 1.0649 | 0.42168
-1.9323 | 0.35981 | 1.1328 | 0.42312
-1.86 | 0.28603 | 1.1906 | 0.42258
-1.7877 | 0.21209 | 1.237 | 0.42163
-1.7154 | 0.13899 | 1.2712 | 0.41864
-1.6431 | 0.067868 | 1.2923 | 0.41277
-1.5708 | 5.5511e-17 | 1.3 | 0.4069
-1.4985 | -0.067868 | 1.2923 | 0.39426
-1.4262 | -0.13899 | 1.2712 | 0.38162
-1.3539 | -0.21209 | 1.237 | 0.36676
-1.2816 | -0.28603 | 1.1906 | 0.35033
-1.2093 | -0.35981 | 1.1328 | 0.33362
-1.137 | -0.43261 | 1.0649 | 0.31561
-1.0647 | -0.50388 | 0.98826 | 0.29759
-0.99234 | -0.57335 | 0.90444 | 0.27989
-0.92004 | -0.64116 | 0.8152 | 0.2623
-0.84773 | -0.7079 | 0.72238 | 0.24491
-0.77542 | -0.77483 | 0.62793 | 0.22794
-0.70312 | -0.84406 | 0.53379 | 0.21097
-0.63081 | -0.91898 | 0.44192 | 0.13525
-0.55851 | -1.0049 | 0.35424 | 0.055174
-0.48869 | -1.1131 | 0.20494 | 0.032114
-0.41888 | -1.0542 | 0.15434 | 0.012679
-0.34907 | -0.98247 | 0.10967 | -0.0028213
-0.31416 | -0.94173 | 0.092489 | -0.0074129
-0.27925 | -0.89333 | 0.075974 | -0.011069
-0.24435 | -0.85472 | 0.060541 | -0.012501
-0.20944 | -0.82348 | 0.046412 | -0.011773
-0.17453 | -0.79541 | 0.03441 | -0.010821
-0.13963 | -0.6365 | 0.025482 | -0.027694
-0.10472 | -0.39095 | 0.01994 | -0.051068
-0.069813 | -0.13071 | 0.016534 | -0.071481
-0.034907 | 0.16173 | 0.01507 | -0.091788
-0.017453 | 0.31121 | 0.01477 | -0.10119
0 | 0.45956 | 0.014649 | -0.10988
0.017453 | 0.60566 | 0.014663 | -0.11776
0.034907 | 0.74868 | 0.014813 | -0.12477
0.05236 | 0.88862 | 0.015072 | -0.13098
0.069813 | 1.0254 | 0.01544 | -0.13648
0.087266 | 1.1588 | 0.015926 | -0.1413
0.10472 | 1.2882 | 0.016541 | -0.1454
0.12217 | 1.4128 | 0.017311 | -0.14875
0.13963 | 1.5309 | 0.01831 | -0.15118
0.15708 | 1.6406 | 0.019631 | -0.15262
0.17453 | 1.7393 | 0.021499 | -0.1531
0.19199 | 1.8197 | 0.024454 | -0.15254
0.20944 | 1.8706 | 0.029662 | -0.15121
0.22689 | 1.8922 | 0.0377 | -0.14969
0.24435 | 1.8791 | 0.048244 | -0.14562
0.2618 | 1.8811 | 0.058376 | -0.14358
0.27925 | 1.8636 | 0.069924 | -0.14095
0.31416 | 1.7332 | 0.10166 | -0.13711
0.34907 | 1.5936 | 0.13916 | -0.14082
0.41888 | 1.4671 | 0.21002 | -0.15693
0.48869 | 1.4483 | 0.282 | -0.17979
0.55851 | 1.4356 | 0.35424 | -0.20147
0.63081 | 1.3128 | 0.44192 | -0.22409
0.70312 | 1.2058 | 0.53379 | -0.24619
0.77542 | 1.1069 | 0.62793 | -0.26133
0.84773 | 1.0113 | 0.72238 | -0.27648
0.92004 | 0.91594 | 0.8152 | -0.29062
0.99234 | 0.81907 | 0.90444 | -0.30424
1.0647 | 0.71982 | 0.98826 | -0.31787
1.137 | 0.61801 | 1.0649 | -0.33154
1.2093 | 0.51401 | 1.1328 | -0.34522
1.2816 | 0.40862 | 1.1906 | -0.35846
1.3539 | 0.30299 | 1.237 | -0.37161
1.4262 | 0.19855 | 1.2712 | -0.38405
1.4985 | 0.096954 | 1.2923 | -0.39547
1.5708 | 8.3267e-17 | 1.3 | -0.4069
1.6431 | -0.067868 | 1.2923 | -0.41277
1.7154 | -0.13899 | 1.2712 | -0.41864
1.7877 | -0.21209 | 1.237 | -0.42163
1.86 | -0.28603 | 1.1906 | -0.42258
1.9323 | -0.35981 | 1.1328 | -0.42312
2.0046 | -0.43261 | 1.0649 | -0.42168
2.0769 | -0.50388 | 0.98826 | -0.42024
2.1492 | -0.57335 | 0.90444 | -0.42058
2.2216 | -0.64116 | 0.8152 | -0.4215
2.2939 | -0.7079 | 0.72238 | -0.42591
2.3662 | -0.77483 | 0.62793 | -0.43697
2.4385 | -0.84406 | 0.53379 | -0.44803
2.5108 | -0.91898 | 0.44192 | -0.46784
2.5831 | -1.0049 | 0.35424 | -0.4883
2.623 | -0.93316 | 0.30832 | -0.496
2.6629 | -0.86138 | 0.26453 | -0.47857
2.7028 | -0.7896 | 0.22313 | -0.46114
2.7427 | -0.71781 | 0.18439 | -0.4437
2.7826 | -0.64603 | 0.14856 | -0.42627
2.8224 | -0.57425 | 0.11586 | -0.4353
2.8623 | -0.50247 | 0.086508 | -0.45315
2.9022 | -0.43069 | 0.060678 | -0.471
2.9421 | -0.35891 | 0.051737 | -0.48884
2.982 | -0.28713 | 0.046531 | -0.45714
3.0219 | -0.21534 | 0.042446 | -0.34286
3.0618 | -0.14356 | 0.039509 | -0.22857
3.1017 | -0.071781 | 0.037739 | -0.11429
3.14 | 0 | 0.037148 | 0

## Blade Support Structure
Span position | Shear web-1 SS s-coord | Shear web-1 PS s-coord | Shear web-2 SS s-coord | Shear web-2 PS s-coord | Spar cap SS begin s-coord | Spar cap SS width [m] | Spar cap SS thick [m] | Spar cap PS begin s-coord | Spar cap PS width [m] | Spar cap PS thick [m] | LE reinf width [m] | LE reinf thick [m] | TE reinf SS width [m] | TE reinf SS thick [m] | TE reinf PS width [m] | TE reinf PS thick [m]
0 | 0.20528 | 0.70808 | 0.20528 | 0.70808 | 0.17774 | 0.9 | 0.0001 | 0.68053 | 0.9 | 0.0001 | 0 | 0 | 0 | 0 | 0 | 0
0.02 | 0.20968 | 0.70371 | 0.20966 | 0.70373 | 0.18217 | 0.89978 | 0.0018695 | 0.67622 | 0.89978 | 0.0018695 | 0.00039013 | 1.4646e-06 | -0.78655 | 6.1082e-06 | -0.78655 | 6.1082e-06
0.020408 | 0.20976 | 0.70365 | 0.20976 | 0.70365 | 0.18225 | 0.89977 | 0.0019253 | 0.67614 | 0.89977 | 0.0019253 | 4.3368e-19 | 0 | -0.79556 | 6.7763e-21 | -0.79556 | 6.7763e-21
0.04 | 0.21382 | 0.70114 | 0.21391 | 0.70105 | 0.18591 | 0.89958 | 0.0056732 | 0.67314 | 0.89958 | 0.0056732 | -0.0014687 | -5.5136e-06 | -0.94978 | -2.2996e-05 | -0.94978 | -2.2996e-05
0.040816 | 0.21403 | 0.70105 | 0.21403 | 0.70105 | 0.18604 | 0.89957 | 0.005878 | 0.67306 | 0.89957 | 0.005878 | 0 | 1.3553e-20 | -0.94556 | 0 | -0.94556 | 0
0.06 | 0.2185 | 0.70083 | 0.21805 | 0.70129 | 0.18918 | 0.8994 | 0.011768 | 0.67196 | 0.8994 | 0.011768 | 0.007374 | 2.7682e-05 | -0.65233 | 0.00011545 | -0.65233 | 0.00011545
0.061224 | 0.2186 | 0.70109 | 0.2186 | 0.70109 | 0.18942 | 0.89939 | 0.012206 | 0.67191 | 0.89939 | 0.012206 | -6.9389e-18 | -2.7105e-20 | -0.62278 | 0 | -0.62278 | 0
0.08 | 0.2237 | 0.70257 | 0.22587 | 0.70038 | 0.19437 | 0.89924 | 0.019635 | 0.67107 | 0.89924 | 0.019635 | -0.035159 | -0.00013199 | -0.056793 | -0.00055049 | -0.056793 | -0.00055049
0.081633 | 0.22544 | 0.7015 | 0.22544 | 0.7015 | 0.19492 | 0.89923 | 0.020338 | 0.67097 | 0.89923 | 0.020338 | -2.7756e-17 | 0 | -4.8572e-17 | -4.3368e-19 | -4.8572e-17 | -4.3368e-19
0.1 | 0.25705 | 0.67818 | 0.21124 | 0.72464 | 0.20251 | 0.8991 | 0.028732 | 0.66948 | 0.8991 | 0.028732 | 0.74109 | 0.0027776 | 0.6742 | 0.012658 | 0.6742 | 0.012658
0.10204 | 0.26003 | 0.67619 | 0.2105 | 0.72644 | 0.20351 | 0.89909 | 0.02971 | 0.66925 | 0.89909 | 0.02971 | 0.8 | 0.0029971 | 0.75 | 0.013973 | 0.75 | 0.013973
0.12245 | 0.27325 | 0.67291 | 0.22215 | 0.72516 | 0.21492 | 0.89897 | 0.039761 | 0.66589 | 0.89897 | 0.039761 | 0.8 | 0.0029679 | 1.4833 | 0.021118 | 1.4833 | 0.021118
0.125 | 0.2746 | 0.67277 | 0.22414 | 0.72439 | 0.21648 | 0.89896 | 0.04103 | 0.66534 | 0.89896 | 0.04103 | 0.7865 | 0.0029133 | 1.5717 | 0.021952 | 1.5717 | 0.021952
0.14286 | 0.28704 | 0.66805 | 0.23489 | 0.72127 | 0.22748 | 0.89887 | 0.049846 | 0.66091 | 0.89887 | 0.049846 | 0.8 | 0.0029388 | 2.1711 | 0.028263 | 2.1711 | 0.028263
0.15 | 0.29161 | 0.66608 | 0.2389 | 0.71976 | 0.23164 | 0.89884 | 0.053306 | 0.65908 | 0.89884 | 0.053306 | 0.80616 | 0.0029518 | 2.4011 | 0.029697 | 2.4011 | 0.029697
0.16327 | 0.29902 | 0.66316 | 0.24644 | 0.71651 | 0.23897 | 0.89879 | 0.059507 | 0.6559 | 0.89879 | 0.059507 | 0.8 | 0.0029096 | 2.8135 | 0.030561 | 2.8135 | 0.030561
0.16903 | 0.30218 | 0.66201 | 0.24959 | 0.71531 | 0.24205 | 0.89876 | 0.062072 | 0.65467 | 0.89876 | 0.062072 | 0.79843 | 0.0028955 | 2.9869 | 0.030562 | 2.9869 | 0.030562
0.18367 | 0.31004 | 0.6592 | 0.25704 | 0.71284 | 0.24951 | 0.89872 | 0.068135 | 0.65184 | 0.89872 | 0.068135 | 0.8 | 0.0028805 | 3.4106 | 0.030249 | 3.4106 | 0.030249
0.18807 | 0.31226 | 0.6584 | 0.25913 | 0.71215 | 0.25159 | 0.89871 | 0.069816 | 0.65103 | 0.89871 | 0.069816 | 0.80037 | 0.0028756 | 3.5333 | 0.030161 | 3.5333 | 0.030161
0.20408 | 0.31965 | 0.65553 | 0.2661 | 0.7097 | 0.25849 | 0.89867 | 0.075179 | 0.64808 | 0.89867 | 0.075179 | 0.8 | 0.0028513 | 3.9626 | 0.03 | 3.9626 | 0.03
0.2071 | 0.32093 | 0.65498 | 0.2673 | 0.70925 | 0.25967 | 0.89866 | 0.076024 | 0.64752 | 0.89866 | 0.076024 | 0.79992 | 0.0028467 | 4.0405 | 0.029991 | 4.0405 | 0.029991
0.22449 | 0.32738 | 0.65218 | 0.27316 | 0.70712 | 0.26544 | 0.89863 | 0.080016 | 0.64467 | 0.89863 | 0.080016 | 0.8 | 0.0028222 | 4.4696 | 0.03 | 4.4696 | 0.03
0.22614 | 0.32788 | 0.65198 | 0.2736 | 0.70698 | 0.26588 | 0.89863 | 0.080341 | 0.64446 | 0.89863 | 0.080341 | 0.80001 | 0.0028199 | 4.5085 | 0.030001 | 4.5085 | 0.030001
0.2449 | 0.33323 | 0.64951 | 0.27811 | 0.70543 | 0.27028 | 0.89861 | 0.083804 | 0.64189 | 0.89861 | 0.083804 | 0.8 | 0.002793 | 4.9315 | 0.03 | 4.9315 | 0.03
0.24517 | 0.33332 | 0.64946 | 0.27819 | 0.7054 | 0.27035 | 0.89861 | 0.083854 | 0.64184 | 0.89861 | 0.083854 | 0.8 | 0.0027926 | 4.9373 | 0.03 | 4.9373 | 0.03
0.26531 | 0.34041 | 0.64469 | 0.28363 | 0.70215 | 0.27556 | 0.8986 | 0.087563 | 0.6368 | 0.8986 | 0.087563 | 0.8 | 0.0027638 | 5.3485 | 0.03 | 5.3485 | 0.03
0.26609 | 0.34066 | 0.64453 | 0.28381 | 0.70205 | 0.27572 | 0.8986 | 0.087702 | 0.63662 | 0.8986 | 0.087702 | 0.8 | 0.0027627 | 5.3636 | 0.03 | 5.3636 | 0.03
0.28571 | 0.34537 | 0.64198 | 0.28684 | 0.70096 | 0.27854 | 0.89861 | 0.090961 | 0.6337 | 0.89861 | 0.090961 | 0.8 | 0.0027347 | 5.7208 | 0.03 | 5.7208 | 0.03
0.28701 | 0.3456 | 0.64189 | 0.28697 | 0.70096 | 0.27865 | 0.89861 | 0.091164 | 0.63359 | 0.89861 | 0.091164 | 0.8 | 0.0027328 | 5.7429 | 0.03 | 5.7429 | 0.03
0.30612 | 0.34832 | 0.64125 | 0.2882 | 0.70156 | 0.27973 | 0.89862 | 0.093942 | 0.63276 | 0.89862 | 0.093942 | 0.8 | 0.0027055 | 6.0483 | 0.03 | 6.0483 | 0.03
0.30793 | 0.34854 | 0.64121 | 0.28828 | 0.70165 | 0.2798 | 0.89862 | 0.094174 | 0.6327 | 0.89862 | 0.094174 | 0.8 | 0.002703 | 6.0751 | 0.03 | 6.0751 | 0.03
0.32653 | 0.35087 | 0.64052 | 0.28913 | 0.70258 | 0.28037 | 0.89865 | 0.096234 | 0.6318 | 0.89865 | 0.096234 | 0.8 | 0.0026764 | 6.3313 | 0.03 | 6.3313 | 0.03
0.32884 | 0.35119 | 0.64037 | 0.28925 | 0.70266 | 0.28045 | 0.89865 | 0.09645 | 0.63163 | 0.89865 | 0.09645 | 0.8 | 0.0026731 | 6.3606 | 0.03 | 6.3606 | 0.03
0.34694 | 0.3541 | 0.63869 | 0.29038 | 0.70278 | 0.28133 | 0.89868 | 0.097775 | 0.62968 | 0.89868 | 0.097775 | 0.8 | 0.0026472 | 6.5698 | 0.03 | 6.5698 | 0.03
0.35091 | 0.35485 | 0.63821 | 0.2907 | 0.70268 | 0.28159 | 0.89869 | 0.097964 | 0.62914 | 0.89869 | 0.097964 | 0.8 | 0.0026416 | 6.611 | 0.03 | 6.611 | 0.03
0.36735 | 0.35814 | 0.63594 | 0.29227 | 0.70196 | 0.28291 | 0.89873 | 0.098363 | 0.62663 | 0.89873 | 0.098363 | 0.8 | 0.0026181 | 6.7638 | 0.03 | 6.7638 | 0.03
0.37298 | 0.35927 | 0.63514 | 0.29283 | 0.70167 | 0.2834 | 0.89874 | 0.098378 | 0.62574 | 0.89874 | 0.098378 | 0.8 | 0.00261 | 6.8095 | 0.03 | 6.8095 | 0.03
0.38776 | 0.36206 | 0.63313 | 0.29424 | 0.70102 | 0.28462 | 0.89878 | 0.0982 | 0.62348 | 0.89878 | 0.0982 | 0.8 | 0.0025889 | 6.9135 | 0.03 | 6.9135 | 0.03
0.39505 | 0.36333 | 0.63224 | 0.29485 | 0.70079 | 0.28513 | 0.8988 | 0.098027 | 0.6225 | 0.8988 | 0.098027 | 0.8 | 0.0025785 | 6.9563 | 0.03 | 6.9563 | 0.03
0.40816 | 0.36538 | 0.63087 | 0.29574 | 0.70059 | 0.28586 | 0.89884 | 0.097577 | 0.62098 | 0.89884 | 0.097577 | 0.8 | 0.0025598 | 7.0191 | 0.03 | 7.0191 | 0.03
0.41711 | 0.36658 | 0.63013 | 0.29619 | 0.70059 | 0.2862 | 0.89886 | 0.097155 | 0.62014 | 0.89886 | 0.097155 | 0.8 | 0.002547 | 7.0514 | 0.03 | 7.0514 | 0.03
0.42857 | 0.36801 | 0.62926 | 0.29662 | 0.70068 | 0.28651 | 0.8989 | 0.096492 | 0.61913 | 0.8989 | 0.096492 | 0.8 | 0.0025306 | 7.0805 | 0.03 | 7.0805 | 0.03
0.43918 | 0.36937 | 0.62837 | 0.297 | 0.70071 | 0.28675 | 0.89894 | 0.095775 | 0.6181 | 0.89894 | 0.095775 | 0.8 | 0.0025155 | 7.095 | 0.03 | 7.095 | 0.03
0.44898 | 0.37081 | 0.62734 | 0.29743 | 0.70059 | 0.28706 | 0.89897 | 0.095049 | 0.61693 | 0.89897 | 0.095049 | 0.8 | 0.0025015 | 7.0978 | 0.03 | 7.0978 | 0.03
0.45888 | 0.3725 | 0.62599 | 0.29802 | 0.70027 | 0.2875 | 0.899 | 0.094273 | 0.61544 | 0.899 | 0.094273 | 0.8 | 0.0024873 | 7.0904 | 0.030001 | 7.0904 | 0.030001
0.46939 | 0.37442 | 0.62439 | 0.29872 | 0.69984 | 0.28805 | 0.89904 | 0.093406 | 0.61368 | 0.89904 | 0.093406 | 0.8 | 0.0024723 | 7.0713 | 0.03 | 7.0713 | 0.03
0.47858 | 0.37605 | 0.62301 | 0.2993 | 0.6995 | 0.28849 | 0.89908 | 0.092617 | 0.61216 | 0.89908 | 0.092617 | 0.8 | 0.0024592 | 7.045 | 0.029995 | 7.045 | 0.029995
0.4898 | 0.3779 | 0.62147 | 0.29987 | 0.69924 | 0.28888 | 0.89912 | 0.091634 | 0.61046 | 0.89912 | 0.091634 | 0.8 | 0.0024431 | 7.0009 | 0.03 | 7.0009 | 0.03
0.49827 | 0.37914 | 0.62049 | 0.30017 | 0.69921 | 0.28904 | 0.89915 | 0.090892 | 0.60937 | 0.89915 | 0.090892 | 0.8 | 0.002431 | 6.9588 | 0.030016 | 6.9588 | 0.030016
0.5102 | 0.38064 | 0.61938 | 0.30037 | 0.6994 | 0.28905 | 0.8992 | 0.089858 | 0.60809 | 0.8992 | 0.089858 | 0.8 | 0.002414 | 6.8868 | 0.03 | 6.8868 | 0.03
0.51797 | 0.38144 | 0.6188 | 0.30038 | 0.69964 | 0.28893 | 0.89923 | 0.089195 | 0.60739 | 0.89923 | 0.089195 | 0.8 | 0.0024029 | 6.8318 | 0.029945 | 6.8318 | 0.029945
0.53061 | 0.3825 | 0.61803 | 0.30015 | 0.70019 | 0.28851 | 0.89928 | 0.088129 | 0.60643 | 0.89928 | 0.088129 | 0.8 | 0.0023848 | 6.729 | 0.03 | 6.729 | 0.03
0.53767 | 0.38298 | 0.61766 | 0.29992 | 0.70056 | 0.28818 | 0.8993 | 0.087537 | 0.60595 | 0.8993 | 0.087537 | 0.8 | 0.0023748 | 6.6643 | 0.030178 | 6.6643 | 0.030178
0.55102 | 0.38388 | 0.6169 | 0.29941 | 0.70122 | 0.28747 | 0.89936 | 0.08641 | 0.60499 | 0.89936 | 0.08641 | 0.8 | 0.0023557 | 6.5277 | 0.029794 | 6.5277 | 0.029794
0.55778 | 0.38441 | 0.61642 | 0.2992 | 0.7015 | 0.28715 | 0.89938 | 0.08583 | 0.6044 | 0.89938 | 0.08583 | 0.8 | 0.002346 | 6.4514 | 0.028748 | 6.4514 | 0.028748
0.57143 | 0.3856 | 0.61533 | 0.29883 | 0.70199 | 0.28656 | 0.89943 | 0.084628 | 0.60308 | 0.89943 | 0.084628 | 0.8 | 0.0023265 | 6.2829 | 0.025671 | 6.2829 | 0.025671
0.57789 | 0.38616 | 0.61482 | 0.29863 | 0.70224 | 0.28625 | 0.89946 | 0.084041 | 0.60245 | 0.89946 | 0.084041 | 0.8 | 0.0023173 | 6.1964 | 0.024299 | 6.1964 | 0.024299
0.59184 | 0.38732 | 0.61376 | 0.29811 | 0.70288 | 0.2855 | 0.89951 | 0.082721 | 0.60116 | 0.89951 | 0.082721 | 0.8 | 0.0022974 | 5.9948 | 0.021549 | 5.9948 | 0.021549
0.59799 | 0.38781 | 0.61334 | 0.29782 | 0.70322 | 0.28513 | 0.89953 | 0.082113 | 0.60064 | 0.89953 | 0.082113 | 0.8 | 0.0022886 | 5.8994 | 0.020253 | 5.8994 | 0.020253
0.61224 | 0.38886 | 0.61245 | 0.29705 | 0.70414 | 0.28413 | 0.89959 | 0.08063 | 0.59955 | 0.89959 | 0.08063 | 0.8 | 0.0022682 | 5.6634 | 0.01704 | 5.6634 | 0.01704
0.6181 | 0.38925 | 0.61213 | 0.2967 | 0.70456 | 0.28368 | 0.89961 | 0.079988 | 0.59914 | 0.89961 | 0.079988 | 0.8 | 0.0022599 | 5.5603 | 0.015691 | 5.5603 | 0.015691
0.63265 | 0.39015 | 0.61141 | 0.29574 | 0.70571 | 0.28245 | 0.89966 | 0.07831 | 0.59819 | 0.89966 | 0.07831 | 0.8 | 0.0022391 | 5.2888 | 0.012273 | 5.2888 | 0.012273
0.63821 | 0.39049 | 0.61114 | 0.29536 | 0.70616 | 0.28195 | 0.89968 | 0.077642 | 0.59783 | 0.89968 | 0.077642 | 0.79998 | 0.0022311 | 5.1794 | 0.010941 | 5.1794 | 0.010941
0.65306 | 0.39137 | 0.61041 | 0.29426 | 0.70745 | 0.28054 | 0.89973 | 0.075746 | 0.59686 | 0.89973 | 0.075746 | 0.79997 | 0.0022099 | 4.8712 | 0.0079507 | 4.8712 | 0.0079507
0.65728 | 0.3916 | 0.6102 | 0.29391 | 0.70783 | 0.2801 | 0.89974 | 0.075169 | 0.59657 | 0.89974 | 0.075169 | 0.8 | 0.0022039 | 4.7794 | 0.0074172 | 4.7794 | 0.0074172
0.67347 | 0.39243 | 0.60939 | 0.29241 | 0.70939 | 0.27827 | 0.89979 | 0.072761 | 0.59548 | 0.89979 | 0.072761 | 0.79983 | 0.0021808 | 4.4106 | 0.0061428 | 4.4106 | 0.0061428
0.67636 | 0.39257 | 0.60924 | 0.29211 | 0.70969 | 0.27791 | 0.8998 | 0.072296 | 0.59529 | 0.8998 | 0.072296 | 0.7997 | 0.0021765 | 4.3419 | 0.0059043 | 4.3419 | 0.0059043
0.69388 | 0.39331 | 0.60841 | 0.29016 | 0.7116 | 0.2756 | 0.89984 | 0.069132 | 0.59412 | 0.89984 | 0.069132 | 0.79848 | 0.0021516 | 3.9072 | 0.004335 | 3.9072 | 0.004335
0.69544 | 0.39338 | 0.60834 | 0.28998 | 0.71178 | 0.27538 | 0.89985 | 0.068814 | 0.59402 | 0.89985 | 0.068814 | 0.79837 | 0.0021495 | 3.8669 | 0.0042241 | 3.8669 | 0.0042241
0.71429 | 0.39406 | 0.60758 | 0.28763 | 0.71409 | 0.27265 | 0.89989 | 0.064216 | 0.59287 | 0.89989 | 0.064216 | 0.79431 | 0.0021224 | 3.3609 | 0.0033935 | 3.3609 | 0.0033935
0.71451 | 0.39407 | 0.60757 | 0.2876 | 0.71412 | 0.27261 | 0.89989 | 0.06415 | 0.59286 | 0.89989 | 0.06415 | 0.79419 | 0.002122 | 3.3546 | 0.0033867 | 3.3546 | 0.0033867
0.73359 | 0.39466 | 0.60702 | 0.28502 | 0.71677 | 0.26964 | 0.89993 | 0.057825 | 0.59189 | 0.89993 | 0.057825 | 0.78175 | 0.0020937 | 2.8049 | 0.0028542 | 2.8049 | 0.0028542
0.73469 | 0.39469 | 0.607 | 0.28486 | 0.71694 | 0.26946 | 0.89993 | 0.057431 | 0.59184 | 0.89993 | 0.057431 | 0.78121 | 0.0020933 | 2.772 | 0.0028233 | 2.772 | 0.0028233
0.75267 | 0.3952 | 0.60666 | 0.28225 | 0.71973 | 0.26647 | 0.89996 | 0.050861 | 0.59109 | 0.89996 | 0.050861 | 0.76543 | 0.0020763 | 2.218 | 0.0022459 | 2.218 | 0.0022459
0.7551 | 0.39527 | 0.60663 | 0.28188 | 0.72013 | 0.26605 | 0.89997 | 0.049944 | 0.59101 | 0.89997 | 0.049944 | 0.75939 | 0.0020641 | 2.1404 | 0.0021512 | 2.1404 | 0.0021512
0.77174 | 0.39571 | 0.60651 | 0.27931 | 0.72301 | 0.26312 | 0.89999 | 0.043549 | 0.59049 | 0.89999 | 0.043549 | 0.72131 | 0.0019965 | 1.594 | 0.0013748 | 1.594 | 0.0013748
0.77551 | 0.39581 | 0.60649 | 0.27871 | 0.72368 | 0.26243 | 0.89999 | 0.042102 | 0.59037 | 0.89999 | 0.042102 | 0.73126 | 0.002035 | 1.4664 | 0.0011734 | 1.4664 | 0.0011734
0.79592 | 0.39647 | 0.60625 | 0.27536 | 0.72741 | 0.25862 | 0.9 | 0.034536 | 0.58961 | 0.9 | 0.034536 | 0.70521 | 0.0020058 | 0.75 | 0.00019556 | 0.75 | 0.00019556
0.8 | 0.3966 | 0.60618 | 0.27465 | 0.72818 | 0.25781 | 0.9 | 0.033101 | 0.58944 | 0.9 | 0.033101 | 0.58723 | 0.0016732 | 0.60171 | 9.7883e-05 | 0.60171 | 9.7883e-05
0.81633 | 0.39715 | 0.60588 | 0.27165 | 0.73139 | 0.25439 | 0.9 | 0.027795 | 0.58867 | 0.9 | 0.027795 | 1.0408e-17 | -5.421e-20 | -4.4409e-16 | -1.8529e-22 | -4.4409e-16 | -1.8529e-22
0.81875 | 0.39723 | 0.60583 | 0.27117 | 0.73188 | 0.25385 | 0.9 | 0.027084 | 0.58854 | 0.9 | 0.027084 | -0.042397 | -0.00012113 | -0.089412 | 4.2107e-07 | -0.089412 | 4.2107e-07
0.83673 | 0.39776 | 0.60538 | 0.26738 | 0.7357 | 0.24955 | 0.9 | 0.022533 | 0.58751 | 0.9 | 0.022533 | 1.301e-17 | -3.3881e-21 | -0.73986 | -1.1911e-22 | -0.73986 | -1.1911e-22
0.8375 | 0.39778 | 0.60536 | 0.26721 | 0.73587 | 0.24936 | 0.9 | 0.022368 | 0.58747 | 0.9 | 0.022368 | 0.0041735 | 1.1924e-05 | -0.76671 | -4.1449e-08 | -0.76671 | -4.1449e-08
0.85625 | 0.3983 | 0.60485 | 0.26271 | 0.7403 | 0.24427 | 0.89999 | 0.01882 | 0.58627 | 0.89999 | 0.01882 | 0.0014921 | 4.263e-06 | -1.3895 | -1.4818e-08 | -1.3895 | -1.4818e-08
0.85714 | 0.39833 | 0.60482 | 0.26248 | 0.74052 | 0.24401 | 0.89999 | 0.018662 | 0.58621 | 0.89999 | 0.018662 | 2.06e-18 | 1.2705e-21 | -1.4171 | -5.6248e-23 | -1.4171 | -5.6248e-23
0.875 | 0.39893 | 0.60419 | 0.25769 | 0.74517 | 0.23866 | 0.89985 | 0.015505 | 0.58489 | 0.89985 | 0.015505 | -0.0012525 | -3.5785e-06 | -1.9172 | 1.2439e-08 | -1.9172 | 1.2439e-08
0.87755 | 0.39899 | 0.60411 | 0.25701 | 0.74584 | 0.23786 | 0.89983 | 0.015067 | 0.58469 | 0.89983 | 0.015067 | 1.3553e-19 | -8.4703e-22 | -1.9794 | 4.1359e-25 | -1.9794 | 4.1359e-25
0.89375 | 0.3995 | 0.60353 | 0.25239 | 0.75028 | 0.23258 | 0.89922 | 0.012403 | 0.58332 | 0.89922 | 0.012403 | 0.00058545 | 1.6727e-06 | -2.309 | -5.8144e-09 | -2.309 | -5.8144e-09
0.89796 | 0.39982 | 0.60318 | 0.25096 | 0.75166 | 0.23116 | 0.89866 | 0.011739 | 0.58294 | 0.89866 | 0.011739 | 1.5585e-19 | 1.8529e-22 | -2.3741 | 6.2039e-25 | -2.3741 | 6.2039e-25
0.9125 | 0.40114 | 0.60175 | 0.2457 | 0.75671 | 0.22624 | 0.89447 | 0.0095238 | 0.58174 | 0.89447 | 0.0095238 | -0.00022419 | -6.4053e-07 | -2.5243 | 2.2265e-09 | -2.5243 | 2.2265e-09
0.91837 | 0.4009 | 0.60194 | 0.24429 | 0.75803 | 0.2244 | 0.89164 | 0.0086739 | 0.58144 | 0.89164 | 0.0086739 | 5.0822e-20 | -3.3087e-23 | -2.5489 | 2.068e-25 | -2.5489 | 2.068e-25
0.93125 | 0.39947 | 0.60326 | 0.242 | 0.76012 | 0.22091 | 0.87996 | 0.0069277 | 0.58146 | 0.87996 | 0.0069277 | 7.6879e-05 | 2.1965e-07 | -2.5224 | -7.6352e-10 | -2.5224 | -7.6352e-10
0.93878 | 0.40225 | 0.60038 | 0.23684 | 0.76509 | 0.21919 | 0.86455 | 0.0060026 | 0.5819 | 0.86455 | 0.0060026 | -1.3553e-20 | -3.9705e-23 | -2.4514 | 2.3264e-25 | -2.4514 | 2.3264e-25
0.95 | 0.4113 | 0.59112 | 0.22393 | 0.77762 | 0.21801 | 0.82247 | 0.0047732 | 0.58414 | 0.82247 | 0.0047732 | -2.4804e-05 | -7.0867e-08 | -2.2626 | 2.4634e-10 | -2.2626 | 2.4634e-10
0.95918 | 0.4038 | 0.59852 | 0.22838 | 0.77307 | 0.22164 | 0.76942 | 0.0038861 | 0.59071 | 0.76942 | 0.0038861 | -8.0468e-21 | -1.4889e-23 | -2.029 | 9.0473e-26 | -2.029 | 9.0473e-26
0.975 | 0.3352 | 0.66721 | 0.29248 | 0.70972 | 0.23567 | 0.6354 | 0.0025689 | 0.61014 | 0.6354 | 0.0025689 | 5.037e-06 | 1.4391e-08 | -1.4449 | -5.0025e-11 | -1.4449 | -5.0025e-11
0.97959 | 0.31317 | 0.68927 | 0.31317 | 0.68927 | 0.23601 | 0.58535 | 0.0022343 | 0.61212 | 0.58535 | 0.0022343 | 0 | 0 | -1.2294 | 0 | -1.2294 | 0
1 | 0.30907 | 0.6929 | 0.30907 | 0.6929 | 0.16803 | 0.294 | 0.001 | 0.55186 | 0.294 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0

## Blade Shell Layup
Airfoil | circular
Pct Span | 0.0
Layer Name | Material | S-coord start | S-coord end | Thickness [mm] | Fiber direction [?]
UV_protection | Gelcoat | 0 | 1 | 1 | 0
Shell_skin | glass_triax | 0 | 1 | 50 | 0
Spar_Cap_SS | CarbonUD | 0.17774 | 0.23283 | 0.1 | 0
Spar_Cap_PS | CarbonUD | 0.68053 | 0.73563 | 0.1 | 0
LE_reinforcement | glass_uni | 0.5 | 0.5 | 0 | 0
TE_reinforcement_SS | glass_uni | 0 | 0 | 0 | 0
TE_reinforcement_PS | glass_uni | 1 | 1 | 0 | 0
TE_SS_filler | medium_density_foam | 0 | 0.17774 | 0 | 0
LE_SS_filler | medium_density_foam | 0.23283 | 0.5 | 0 | 0
LE_PS_filler | medium_density_foam | 0.5 | 0.68053 | 0 | 0
TE_PS_filler | medium_density_foam | 0.73563 | 1 | 0 | 0
Shell_skin_inner | glass_triax | 0 | 1 | 50 | 0
Airfoil | circular
Pct Span | 2.0
Layer Name | Material | S-coord start | S-coord end | Thickness [mm] | Fiber direction [?]
UV_protection | Gelcoat | 0 | 1 | 1 | 0
Shell_skin | glass_triax | 3.7832e-12 | 1 | 44.5948 | 0
Spar_Cap_SS | CarbonUD | 0.18213 | 0.23716 | 1.9014 | 0
Spar_Cap_PS | CarbonUD | 0.67629 | 0.73132 | 1.9014 | 0
LE_reinforcement | glass_uni | 0.49998 | 0.50002 | 0.002401 | 0
TE_reinforcement_SS | glass_uni | 0 | 4.2495e-05 | 0.010608 | 0
TE_reinforcement_PS | glass_uni | 0.99996 | 1 | 0.010608 | 0
TE_SS_filler | medium_density_foam | 4.2495e-05 | 0.18213 | 0.048126 | 0
LE_SS_filler | medium_density_foam | 0.23716 | 0.49998 | 0.048126 | 0
LE_PS_filler | medium_density_foam | 0.50002 | 0.67629 | 0.048126 | 0
TE_PS_filler | medium_density_foam | 0.73132 | 0.99996 | 0.048126 | 0
Shell_skin_inner | glass_triax | -1.6544e-09 | 1 | 44.5948 | 0
Airfoil | SNL-FFA-W3-500
Pct Span | 15.0
Layer Name | Material | S-coord start | S-coord end | Thickness [mm] | Fiber direction [?]
UV_protection | Gelcoat | 0 | 1 | 1 | 0
Shell_skin | glass_triax | -4.6392e-08 | 1 | 13.0107 | 0
Spar_Cap_SS | CarbonUD | 0.2316 | 0.29869 | 53.3096 | 0
Spar_Cap_PS | CarbonUD | 0.65903 | 0.72613 | 53.3096 | 0
LE_reinforcement | glass_uni | 0.46873 | 0.52848 | 2.9346 | 0
TE_reinforcement_SS | glass_uni | 0 | 0.056017 | 29.4844 | 0
TE_reinforcement_PS | glass_uni | 0.94398 | 1 | 29.4844 | 0
TE_SS_filler | medium_density_foam | 0.056017 | 0.2316 | 56.192 | 0
LE_SS_filler | medium_density_foam | 0.29869 | 0.46873 | 56.192 | 0
LE_PS_filler | medium_density_foam | 0.52848 | 0.65903 | 56.192 | 0
TE_PS_filler | medium_density_foam | 0.72613 | 0.94398 | 56.192 | 0
Shell_skin_inner | glass_triax | 2.0287e-05 | 0.99998 | 13.0107 | 0
Airfoil | FFA-W3-360
Pct Span | 24.517031675566095
Layer Name | Material | S-coord start | S-coord end | Thickness [mm] | Fiber direction [?]
UV_protection | Gelcoat | 0 | 1 | 1 | 0
Shell_skin | glass_triax | -0.00014671 | 1.0001 | 3.005 | 0
Spar_Cap_SS | CarbonUD | 0.27052 | 0.34131 | 83.8876 | 0
Spar_Cap_PS | CarbonUD | 0.64163 | 0.71242 | 83.8876 | 0
LE_reinforcement | glass_uni | 0.46883 | 0.53176 | 2.7926 | 0
TE_reinforcement_SS | glass_uni | 0 | 0.058996 | 29.9992 | 0
TE_reinforcement_PS | glass_uni | 0.941 | 1 | 29.9992 | 0
TE_SS_filler | medium_density_foam | 0.058996 | 0.27052 | 48.5939 | 0
LE_SS_filler | medium_density_foam | 0.34131 | 0.46883 | 48.5939 | 0
LE_PS_filler | medium_density_foam | 0.53176 | 0.64163 | 48.5939 | 0
TE_PS_filler | medium_density_foam | 0.71242 | 0.941 | 48.5939 | 0
Shell_skin_inner | glass_triax | 0.076227 | 0.92377 | 3.005 | 0
Airfoil | FFA-W3-330blend
Pct Span | 32.884395064724345
Layer Name | Material | S-coord start | S-coord end | Thickness [mm] | Fiber direction [?]
UV_protection | Gelcoat | 0 | 1 | 1 | 0
Shell_skin | glass_triax | 0.009988 | 0.99001 | 2.004 | 0
Spar_Cap_SS | CarbonUD | 0.28045 | 0.35992 | 96.4717 | 0
Spar_Cap_PS | CarbonUD | 0.63162 | 0.7111 | 96.4717 | 0
LE_reinforcement | glass_uni | 0.46592 | 0.53656 | 2.6731 | 0
TE_reinforcement_SS | glass_uni | 0 | 0.066226 | 30 | 0
TE_reinforcement_PS | glass_uni | 0.93377 | 1 | 30 | 0
TE_SS_filler | medium_density_foam | 0.066226 | 0.28045 | 42.0194 | 0
LE_SS_filler | medium_density_foam | 0.35992 | 0.46592 | 42.0194 | 0
LE_PS_filler | medium_density_foam | 0.53656 | 0.63162 | 42.0194 | 0
TE_PS_filler | medium_density_foam | 0.7111 | 0.93377 | 42.0194 | 0
Shell_skin_inner | glass_triax | 0.080003 | 0.92 | 2.004 | 0
Airfoil | FFA-W3-301
Pct Span | 43.91793464459161
Layer Name | Material | S-coord start | S-coord end | Thickness [mm] | Fiber direction [?]
UV_protection | Gelcoat | 0 | 1 | 1 | 0
Shell_skin | glass_triax | 0.01 | 0.99 | 2 | 0
Spar_Cap_SS | CarbonUD | 0.28674 | 0.37946 | 95.7766 | 0
Spar_Cap_PS | CarbonUD | 0.61813 | 0.71085 | 95.7766 | 0
LE_reinforcement | glass_uni | 0.46044 | 0.54286 | 2.5155 | 0
TE_reinforcement_SS | glass_uni | 0 | 0.077267 | 30 | 0
TE_reinforcement_PS | glass_uni | 0.92273 | 1 | 30 | 0
TE_SS_filler | medium_density_foam | 0.077267 | 0.28674 | 33.3502 | 0
LE_SS_filler | medium_density_foam | 0.37946 | 0.46044 | 33.3502 | 0
LE_PS_filler | medium_density_foam | 0.54286 | 0.61813 | 33.3502 | 0
TE_PS_filler | medium_density_foam | 0.71085 | 0.92273 | 33.3502 | 0
Shell_skin_inner | glass_triax | 0.08 | 0.92 | 2 | 0
Airfoil | FFA-W3-270blend
Pct Span | 53.76714071084352
Layer Name | Material | S-coord start | S-coord end | Thickness [mm] | Fiber direction [?]
UV_protection | Gelcoat | 0 | 1 | 1 | 0
Shell_skin | glass_triax | 0.01 | 0.99 | 2 | 0
Spar_Cap_SS | CarbonUD | 0.28815 | 0.39447 | 87.5377 | 0
Spar_Cap_PS | CarbonUD | 0.60598 | 0.71229 | 87.5377 | 0
LE_reinforcement | glass_uni | 0.45327 | 0.54778 | 2.3748 | 0
TE_reinforcement_SS | glass_uni | 0 | 0.088597 | 29.9878 | 0
TE_reinforcement_PS | glass_uni | 0.9114 | 1 | 29.9878 | 0
TE_SS_filler | medium_density_foam | 0.088597 | 0.28815 | 25.6115 | 0
LE_SS_filler | medium_density_foam | 0.39447 | 0.45327 | 25.6115 | 0
LE_PS_filler | medium_density_foam | 0.54778 | 0.60598 | 25.6115 | 0
TE_PS_filler | medium_density_foam | 0.71229 | 0.9114 | 25.6115 | 0
Shell_skin_inner | glass_triax | 0.08 | 0.92 | 2 | 0
Airfoil | FFA-W3-241
Pct Span | 63.82076569163737
Layer Name | Material | S-coord start | S-coord end | Thickness [mm] | Fiber direction [?]
UV_protection | Gelcoat | 0 | 1 | 1 | 0
Shell_skin | glass_triax | 0.01 | 0.99 | 2 | 0
Spar_Cap_SS | CarbonUD | 0.28196 | 0.40375 | 77.6452 | 0
Spar_Cap_PS | CarbonUD | 0.59783 | 0.71962 | 77.6452 | 0
LE_reinforcement | glass_uni | 0.44484 | 0.5531 | 2.2311 | 0
TE_reinforcement_SS | glass_uni | 0 | 0.10149 | 10.85 | 0
TE_reinforcement_PS | glass_uni | 0.89851 | 1 | 10.85 | 0
TE_SS_filler | medium_density_foam | 0.10149 | 0.28196 | 17.7123 | 0
LE_SS_filler | medium_density_foam | 0.40375 | 0.44484 | 17.7123 | 0
LE_PS_filler | medium_density_foam | 0.5531 | 0.59783 | 17.7123 | 0
TE_PS_filler | medium_density_foam | 0.71962 | 0.89851 | 17.7123 | 0
Shell_skin_inner | glass_triax | 0.08 | 0.92 | 2 | 0
Airfoil | FFA-W3-211
Pct Span | 77.17438522715817
Layer Name | Material | S-coord start | S-coord end | Thickness [mm] | Fiber direction [?]
UV_protection | Gelcoat | 0 | 1 | 1 | 0
Shell_skin | glass_triax | 0.01 | 0.99 | 1.9986 | 0
Spar_Cap_SS | CarbonUD | 0.26312 | 0.41211 | 43.5575 | 0
Spar_Cap_PS | CarbonUD | 0.59048 | 0.73947 | 43.5575 | 0
LE_reinforcement | glass_uni | 0.43736 | 0.55632 | 1.9902 | 0
TE_reinforcement_SS | glass_uni | 0 | 0.12077 | 1.3706 | 0
TE_reinforcement_PS | glass_uni | 0.87923 | 1 | 1.3706 | 0
TE_SS_filler | medium_density_foam | 0.12077 | 0.26312 | 7.1346 | 0
LE_SS_filler | medium_density_foam | 0.41211 | 0.43736 | 7.1346 | 0
LE_PS_filler | medium_density_foam | 0.55632 | 0.59048 | 7.1346 | 0
TE_PS_filler | medium_density_foam | 0.73947 | 0.87923 | 7.1346 | 0
Shell_skin_inner | glass_triax | 0.08 | 0.92 | 1.9986 | 0
Airfoil | FFA-W3-211
Pct Span | 100.0
Layer Name | Material | S-coord start | S-coord end | Thickness [mm] | Fiber direction [?]
UV_protection | Gelcoat | 0 | 1 | 1 | 0
Shell_skin | glass_triax | 0.01 | 0.99 | 1 | 0
Spar_Cap_SS | CarbonUD | 0.16803 | 0.4501 | 1 | 0
Spar_Cap_PS | CarbonUD | 0.55186 | 0.83394 | 1 | 0
LE_reinforcement | glass_uni | 0.49684 | 0.49684 | 0 | 0
TE_reinforcement_SS | glass_uni | 0 | 0 | 0 | 0
TE_reinforcement_PS | glass_uni | 1 | 1 | 0 | 0
TE_SS_filler | medium_density_foam | 0 | 0.16803 | 0 | 0
LE_SS_filler | medium_density_foam | 0.4501 | 0.49684 | 0 | 0
LE_PS_filler | medium_density_foam | 0.49684 | 0.55186 | 0 | 0
TE_PS_filler | medium_density_foam | 0.83394 | 1 | 0 | 0
Shell_skin_inner | glass_triax | 0.08 | 0.92 | 1 | 0

## Shear Web Layup
Airfoil | circular
Pct Span | 0.0
Shear web | Layer Name | Material | Thickness [mm] | Fiber direction [?]
Airfoil | circular
Pct Span | 2.0
Shear web | Layer Name | Material | Thickness [mm] | Fiber direction [?]
web0 | web0_skinLE | glass_biax | 0.0016024 | 0
web0 | web0_filler | medium_density_foam | 0.034466 | 0
web0 | web0_skinTE | glass_biax | 0.0016024 | 0
web1 | web1_skinLE | glass_biax | 0.0016024 | 0
web1 | web1_filler | medium_density_foam | 0.034466 | 0
web1 | web1_skinTE | glass_biax | 0.0016024 | 0
Airfoil | SNL-FFA-W3-500
Pct Span | 15.0
Shear web | Layer Name | Material | Thickness [mm] | Fiber direction [?]
web0 | web0_skinLE | glass_biax | 1.9158 | 0
web0 | web0_filler | medium_density_foam | 40.8511 | 0
web0 | web0_skinTE | glass_biax | 1.9158 | 0
web1 | web1_skinLE | glass_biax | 1.9158 | 0
web1 | web1_filler | medium_density_foam | 40.8511 | 0
web1 | web1_skinTE | glass_biax | 1.9158 | 0
Airfoil | FFA-W3-360
Pct Span | 24.517031675566095
Shear web | Layer Name | Material | Thickness [mm] | Fiber direction [?]
web0 | web0_skinLE | glass_biax | 1.7438 | 0
web0 | web0_filler | medium_density_foam | 36.5101 | 0
web0 | web0_skinTE | glass_biax | 1.7438 | 0
web1 | web1_skinLE | glass_biax | 1.7438 | 0
web1 | web1_filler | medium_density_foam | 36.5101 | 0
web1 | web1_skinTE | glass_biax | 1.7438 | 0
Airfoil | FFA-W3-330blend
Pct Span | 32.884395064724345
Shear web | Layer Name | Material | Thickness [mm] | Fiber direction [?]
web0 | web0_skinLE | glass_biax | 1.5962 | 0
web0 | web0_filler | medium_density_foam | 32.7693 | 0
web0 | web0_skinTE | glass_biax | 1.5962 | 0
web1 | web1_skinLE | glass_biax | 1.5962 | 0
web1 | web1_filler | medium_density_foam | 32.7693 | 0
web1 | web1_skinTE | glass_biax | 1.5962 | 0
Airfoil | FFA-W3-301
Pct Span | 43.91793464459161
Shear web | Layer Name | Material | Thickness [mm] | Fiber direction [?]
web0 | web0_skinLE | glass_biax | 1.4014 | 0
web0 | web0_filler | medium_density_foam | 27.8367 | 0
web0 | web0_skinTE | glass_biax | 1.4014 | 0
web1 | web1_skinLE | glass_biax | 1.4014 | 0
web1 | web1_filler | medium_density_foam | 27.8367 | 0
web1 | web1_skinTE | glass_biax | 1.4014 | 0
Airfoil | FFA-W3-270blend
Pct Span | 53.76714071084352
Shear web | Layer Name | Material | Thickness [mm] | Fiber direction [?]
web0 | web0_skinLE | glass_biax | 1.2276 | 0
web0 | web0_filler | medium_density_foam | 23.4332 | 0
web0 | web0_skinTE | glass_biax | 1.2276 | 0
web1 | web1_skinLE | glass_biax | 1.2276 | 0
web1 | web1_filler | medium_density_foam | 23.4332 | 0
web1 | web1_skinTE | glass_biax | 1.2276 | 0
Airfoil | FFA-W3-241
Pct Span | 63.82076569163737
Shear web | Layer Name | Material | Thickness [mm] | Fiber direction [?]
web0 | web0_skinLE | glass_biax | 1.0502 | 0
web0 | web0_filler | medium_density_foam | 20.0065 | 0
web0 | web0_skinTE | glass_biax | 1.0502 | 0
web1 | web1_skinLE | glass_biax | 1.0502 | 0
web1 | web1_filler | medium_density_foam | 20.0065 | 0
web1 | web1_skinTE | glass_biax | 1.0502 | 0
Airfoil | FFA-W3-211
Pct Span | 77.17438522715817
Shear web | Layer Name | Material | Thickness [mm] | Fiber direction [?]
web0 | web0_skinLE | glass_biax | 0.81457 | 0
web0 | web0_filler | medium_density_foam | 20 | 0
web0 | web0_skinTE | glass_biax | 0.81457 | 0
web1 | web1_skinLE | glass_biax | 0.81457 | 0
web1 | web1_filler | medium_density_foam | 20 | 0
web1 | web1_skinTE | glass_biax | 0.81457 | 0
Airfoil | FFA-W3-211
Pct Span | 100.0
Shear web | Layer Name | Material | Thickness [mm] | Fiber direction [?]

## Blade Structural Properties
BeamDyn Coordinate System (see https://wind.nrel.gov/nwtc/docs/BeamDyn_Manual.pdf)
| M_11 | M_12 | M_13 | M_14 | M_15 | M_16 | M_22 | M_23 | M_24 | M_25 | M_26 | M_33 | M_34 | M_35 | M_36 | M_44 | M_45 | M_46 | M_55 | M_56 | M_66 | K_11 | K_12 | K_13 | K_14 | K_15 | K_16 | K_22 | K_23 | K_24 | K_25 | K_26 | K_33 | K_34 | K_35 | K_36 | K_44 | K_45 | K_46 | K_55 | K_56 | K_66
0 | 3127.4021 | 0 | 0 | 0 | 0 | 73.932 | 3127.4021 | 0 | 0 | 0 | -0.23228 | 3127.4021 | -73.932 | 0.23228 | 0 | 10167.9763 | 1.0683 | 0 | 10166.2844 | 0 | 20334.2607 | 6740375994.2008 | 2653738.5919 | 0 | 0 | 0 | 148446683.0081 | 6729088765.3959 | 0 | 0 | 0 | 38985021.6652 | 46051081603.6047 | -1092494742.1422 | 18829097.3029 | 0 | 149629012637.9659 | -22581466.1652 | 0 | 149729095916.4146 | 0 | 87489183048.0329
0.01 | 2964.7325 | 0 | 0 | 0 | 0 | -39.6893 | 2964.7325 | 0 | 0 | 0 | -0.16965 | 2964.7325 | 39.6893 | 0.16965 | 0 | 9670.8175 | -0.9134 | 0 | 9677.5067 | 0 | 19348.3241 | 6384592445.5102 | -376400.6474 | 0 | 0 | 0 | -93807158.5472 | 6388480690.3107 | 0 | 0 | 0 | 16608264.9357 | 43751344063.1982 | 582609637.8397 | 3336008.2994 | 0 | 142328864112.5016 | -232559270.0609 | 0 | 143137826352.7965 | 0 | 83285587642.8216
0.02 | 2805.1273 | 0 | 0 | 0 | 0 | -140.7515 | 2805.1273 | 0 | 0 | 0 | 2.4057 | 2805.1273 | 140.7515 | -2.4057 | 0 | 9183.7237 | -6.1434 | 0 | 9189.9792 | 0 | 18373.7029 | 6033428473.0283 | -5351360.1271 | 0 | 0 | 0 | -302258358.4147 | 6055417688.5154 | 0 | 0 | 0 | 5594870.1147 | 41569662567.4704 | 2071574619.5397 | -39669072.5379 | 0 | 135212838311.3875 | -606773042.4006 | 0 | 137008541712.7096 | 0 | 79106159653.8364
0.03 | 2591.1368 | 0 | 0 | 0 | 0 | -186.5071 | 2591.1368 | 0 | 0 | 0 | 8.8503 | 2591.1368 | 186.5071 | -8.8503 | 0 | 8366.6705 | -30.176 | 0 | 7913.5551 | 0 | 16280.2257 | 5399937528.5607 | 2545105.3702 | 0 | 0 | 0 | -376430490.911 | 5758216767.8686 | 0 | 0 | 0 | 19709135.8539 | 38669982721.7398 | 2739604966.9814 | -139140684.301 | 0 | 123284345388.3974 | -1348337968.6179 | 0 | 119514275124.8942 | 0 | 69973323042.1117
0.04 | 2389.1154 | 0 | 0 | 0 | 0 | -225.6725 | 2389.1154 | 0 | 0 | 0 | 12.7298 | 2389.1154 | 225.6725 | -12.7298 | 0 | 7605.9992 | -51.1381 | 0 | 6778.7079 | 0 | 14384.7071 | 4800672070.8924 | 6445969.8453 | 0 | 0 | 0 | -410026336.0979 | 5468722459.9552 | 0 | 0 | 0 | 28462348.9384 | 36038990116.7374 | 3310499851.2371 | -201959858.6631 | 0 | 112223397786.614 | -2131730557.8957 | 0 | 104365370041.9754 | 0 | 61533150488.5011
0.05 | 2203.5225 | 0 | 0 | 0 | 0 | -266.6698 | 2203.5225 | 0 | 0 | 0 | 15.7762 | 2203.5225 | 266.6698 | -15.7762 | 0 | 6947.0217 | -69.3429 | 0 | 5816.7305 | 0 | 12763.7522 | 4245595846.6039 | 6455163.7024 | 0 | 0 | 0 | -423187047.4596 | 5195984070.2949 | 0 | 0 | 0 | 35814075.9438 | 33746441410.1962 | 3921047165.8378 | -248900545.3029 | 0 | 102686583994.1113 | -2938603122.2992 | 0 | 91978034767.2062 | 0 | 54135840079.7236
0.075 | 1793.5622 | 0 | 0 | 0 | 0 | -349.6389 | 1793.5622 | 0 | 0 | 0 | 21.3206 | 1793.5622 | 349.6389 | -21.3206 | 0 | 5542.222 | -103.2819 | 0 | 3914.5968 | 0 | 9456.8188 | 3015180949.0748 | -6056529.37 | 0 | 0 | 0 | -335581833.1749 | 4552086385.1725 | 0 | 0 | 0 | 53346766.102 | 29212071034.7307 | 5225114500.3669 | -316621483.9665 | 0 | 82456226297.9696 | -4823615805.8995 | 0 | 68686121530.6874 | 0 | 38418612295.4395
0.1 | 1694.5071 | 0 | 0 | 0 | 0 | -525.431 | 1694.5071 | 0 | 0 | 0 | 33.6315 | 1694.5071 | 525.431 | -33.6315 | 0 | 4883.6116 | -159.4225 | 0 | 2785.9557 | 0 | 7669.5673 | 2419253237.9809 | 113285786.0036 | 0 | 0 | 0 | -235382612.4996 | 3985354344.8682 | 0 | 0 | 0 | 87781196.9179 | 27339201435.2974 | 8519455804.0232 | -518317006.659 | 0 | 72781368868.3972 | -6133557676.8317 | 0 | 52263394041.3747 | 0 | 25428346793.2585
0.15 | 1050.5042 | 0 | 0 | 0 | 0 | -610.1712 | 1050.5042 | 0 | 0 | 0 | 24.4884 | 1050.5042 | 610.1712 | -24.4884 | 0 | 3320.8865 | -109.4124 | 0 | 956.3089 | 0 | 4277.1954 | 936314786.8968 | 80833117.6725 | 0 | 0 | 0 | 110222775.8261 | 2314391966.6611 | 0 | 0 | 0 | 102518319.262 | 22665764106.8517 | 10699908369.6695 | -252339646.0121 | 0 | 54125167812.0393 | -4839685559.4882 | 0 | 27988353518.8597 | 0 | 8076640558.8585
0.2 | 668.8389 | 0 | 0 | 0 | 0 | -519.3241 | 668.8389 | 0 | 0 | 0 | 20.2751 | 668.8389 | 519.3241 | -20.2751 | 0 | 2253.5587 | -74.2566 | 0 | 476.3637 | 0 | 2729.9223 | 459476847.2247 | 50723215.9636 | 0 | 0 | 0 | 44624062.1146 | 963021463.3416 | 0 | 0 | 0 | 63418511.8548 | 20450235425.961 | 9176487472.148 | -318201927.7338 | 0 | 39196915729.859 | -3395447917.8744 | 0 | 21820483410.1577 | 0 | 2768066330.9733
0.25 | 531.0613 | 0 | 0 | 0 | 0 | -469.1873 | 531.0613 | 0 | 0 | 0 | 18.4069 | 531.0613 | 469.1873 | -18.4069 | 0 | 1848.5784 | -51.0005 | 0 | 268.5595 | 0 | 2117.1379 | 281350049.4487 | 19062499.8909 | 0 | 0 | 0 | 39788481.5584 | 480065126.6654 | 0 | 0 | 0 | 35649958.0014 | 20473859852.029 | 9004633626.1688 | -370375609.6292 | 0 | 35299428705.2673 | -1524671060.6524 | 0 | 15615256841.1064 | 0 | 1026128471.8607
0.3 | 483.9852 | 0 | 0 | 0 | 0 | -429.5474 | 483.9852 | 0 | 0 | 0 | 15.2494 | 483.9852 | 429.5474 | -15.2494 | 0 | 1564.736 | -34.0708 | 0 | 204.0677 | 0 | 1768.8037 | 224644322.0169 | 4177613.4992 | 0 | 0 | 0 | 22822651.1063 | 346901262.3854 | 0 | 0 | 0 | 26944490.4842 | 21366371296.473 | 8306288511.8529 | -349173302.5919 | 0 | 31051165577.5574 | -615674444.314 | 0 | 13362814423.3876 | 0 | 627053086.269
0.35 | 458.0839 | 0 | 0 | 0 | 0 | -387.9979 | 458.0839 | 0 | 0 | 0 | 12.5415 | 458.0839 | 387.9979 | -12.5415 | 0 | 1286.7176 | -23.3864 | 0 | 154.7472 | 0 | 1441.4648 | 187672692.5729 | -2993741.6568 | 0 | 0 | 0 | 14817252.655 | 324078740.9094 | 0 | 0 | 0 | 22977520.6769 | 21785402237.0392 | 7885934214.4209 | -281941707.0511 | 0 | 26088284004.5495 | -91553134.3129 | 0 | 10663481378.1392 | 0 | 461211585.4908
0.4 | 433.8716 | 0 | 0 | 0 | 0 | -345.8892 | 433.8716 | 0 | 0 | 0 | 9.3851 | 433.8716 | 345.8892 | -9.3851 | 0 | 1076.1433 | -18.7515 | 0 | 120.163 | 0 | 1196.3063 | 161609316.9018 | -3309906.6226 | 0 | 0 | 0 | 14196051.9459 | 317531903.3032 | 0 | 0 | 0 | 19104038.4869 | 21621041012.0421 | 6912268845.2774 | -151464382.0873 | 0 | 22217425410.9591 | -10375272.8535 | 0 | 8537806429.6815 | 0 | 364794590.1572
0.45 | 404.9178 | 0 | 0 | 0 | 0 | -311.0719 | 404.9178 | 0 | 0 | 0 | 7.4758 | 404.9178 | 311.0719 | -7.4758 | 0 | 895.7514 | -15.6036 | 0 | 90.5085 | 0 | 986.2599 | 137969183.9902 | -2612569.6185 | 0 | 0 | 0 | 10110737.4144 | 309152872.5553 | 0 | 0 | 0 | 15276680.6011 | 20779461548.7558 | 6380607368.4177 | -81958836.226 | 0 | 18717308525.7936 | 2259343.5051 | 0 | 6549534664.5338 | 0 | 285660364.0989
0.5 | 377.7312 | 0 | 0 | 0 | 0 | -272.8501 | 377.7312 | 0 | 0 | 0 | 7.8156 | 377.7312 | 272.8501 | -7.8156 | 0 | 735.4079 | -13.6442 | 0 | 66.5159 | 0 | 801.9238 | 116600478.4524 | -1443459.8265 | 0 | 0 | 0 | 9756447.0757 | 303218881.8212 | 0 | 0 | 0 | 12426129.2123 | 19923519424.8057 | 5510503208.4827 | -145792800.1543 | 0 | 15586807919.0939 | -28845801.8403 | 0 | 4893346064.3231 | 0 | 220544333.375
0.55 | 350.4843 | 0 | 0 | 0 | 0 | -237.9795 | 350.4843 | 0 | 0 | 0 | 8.183 | 350.4843 | 237.9795 | -8.183 | 0 | 593.1078 | -11.6623 | 0 | 48.3879 | 0 | 641.4957 | 97422515.9833 | -997091.0381 | 0 | 0 | 0 | 7650615.7891 | 292909738.4692 | 0 | 0 | 0 | 11590547.0254 | 18925122694.7134 | 4939813431.1543 | -215770838.7096 | 0 | 12739863625.7452 | -43922352.519 | 0 | 3604017503.6992 | 0 | 168037150.4417
0.6 | 307.3478 | 0 | 0 | 0 | 0 | -164.7292 | 307.3478 | 0 | 0 | 0 | 7.9517 | 307.3478 | 164.7292 | -7.9517 | 0 | 389.1097 | -7.837 | 0 | 35.2222 | 0 | 424.3318 | 81358328.9585 | 122590.7089 | 0 | 0 | 0 | 7709138.6346 | 300285135.273 | 0 | 0 | 0 | 12779793.3656 | 17539655765.2353 | 3340368066.197 | -299940988.5742 | 0 | 8379809772.7363 | -29747619.2878 | 0 | 2655217532.0577 | 0 | 128226839.007
0.65 | 260.2653 | 0 | 0 | 0 | 0 | -93.4347 | 260.2653 | 0 | 0 | 0 | 7.2927 | 260.2653 | 93.4347 | -7.2927 | 0 | 215.4694 | -4.1761 | 0 | 25.2155 | 0 | 240.6849 | 67080158.8242 | 1150059.0012 | 0 | 0 | 0 | 8354890.6717 | 334604810.692 | 0 | 0 | 0 | 15336313.59 | 15853197990.9463 | 1772039285.1553 | -358354291.3769 | 0 | 4637021573.4688 | -2424421.8977 | 0 | 1917970315.4393 | 0 | 95377930.582
0.7 | 223.9426 | 0 | 0 | 0 | 0 | -57.935 | 223.9426 | 0 | 0 | 0 | 7.223 | 223.9426 | 57.935 | -7.223 | 0 | 131.6545 | -2.6421 | 0 | 17.7453 | 0 | 149.3999 | 55553240.5837 | 1941394.5823 | 0 | 0 | 0 | 8124277.1876 | 376257910.1037 | 0 | 0 | 0 | 18041654.7782 | 14061229868.5256 | 1013471013.8503 | -411634704.483 | 0 | 2889083609.8506 | -12258851.3476 | 0 | 1351951128.6929 | 0 | 71456369.556
0.75 | 179.5841 | 0 | 0 | 0 | 0 | -38.0524 | 179.5841 | 0 | 0 | 0 | 6.5724 | 179.5841 | 38.0524 | -6.5724 | 0 | 84.6496 | -1.7996 | 0 | 11.2712 | 0 | 95.9208 | 44994384.5687 | 2180662.5762 | 0 | 0 | 0 | 7061108.3534 | 395913126.7682 | 0 | 0 | 0 | 19527620.3355 | 11003024089.7932 | 625226575.7819 | -386594144.7272 | 0 | 1877272361.9364 | -15695344.2666 | 0 | 838106592.7415 | 0 | 52519301.1763
0.8 | 129.308 | 0 | 0 | 0 | 0 | -23.226 | 129.308 | 0 | 0 | 0 | 4.7192 | 129.308 | 23.226 | -4.7192 | 0 | 51.4548 | -1.0405 | 0 | 6.6846 | 0 | 58.1394 | 36509915.3833 | 2151842.3144 | 0 | 0 | 0 | 6124281.7512 | 375210610.3003 | 0 | 0 | 0 | 17825049.8174 | 7310260724.8634 | 354179115.2888 | -261309728.4736 | 0 | 1099701983.6863 | -6469059.3112 | 0 | 466233432.8813 | 0 | 38106482.5137
0.85 | 84.4557 | 0 | 0 | 0 | 0 | -16.3955 | 84.4557 | 0 | 0 | 0 | 2.8211 | 84.4557 | 16.3955 | -2.8211 | 0 | 31.5075 | -0.62321 | 0 | 3.6163 | 0 | 35.1239 | 27272722.3361 | 993432.1718 | 0 | 0 | 0 | 3331136.3124 | 239673891.333 | 0 | 0 | 0 | 10738401.6327 | 4521289678.947 | 266089109.403 | -148760396.9854 | 0 | 683571619.6771 | -4841801.2367 | 0 | 243066553.4405 | 0 | 23330158.8618
0.9 | 54.7047 | 0 | 0 | 0 | 0 | -11.0332 | 54.7047 | 0 | 0 | 0 | 1.6418 | 54.7047 | 11.0332 | -1.6418 | 0 | 19.3199 | -0.36849 | 0 | 1.7833 | 0 | 21.1032 | 19745236.354 | 510321.8004 | 0 | 0 | 0 | 1832045.8992 | 144312493.8659 | 0 | 0 | 0 | 6016948.8977 | 2675615584.1351 | 184789087.6841 | -79832450.7483 | 0 | 420297066.7673 | -4125365.2248 | 0 | 113253467.9701 | 0 | 13417874.4622
0.95 | 34.4499 | 0 | 0 | 0 | 0 | -8.1195 | 34.4499 | 0 | 0 | 0 | 0.91651 | 34.4499 | 8.1195 | -0.91651 | 0 | 12.2628 | -0.24956 | 0 | 0.75738 | 0 | 13.0202 | 9179700.6757 | 307950.6174 | 0 | 0 | 0 | 1267110.0781 | 86939021.6748 | 0 | 0 | 0 | 3396279.8195 | 1203040036.1543 | 137345812.7563 | -31896540.3793 | 0 | 231512293.7071 | -3561131.7253 | 0 | 36395660.0209 | 0 | 6805118.0907
1 | 5.395 | 0 | 0 | 0 | 0 | -0.15889 | 5.395 | 0 | 0 | 0 | 0.036961 | 5.395 | 0.15889 | -0.036961 | 0 | 0.093734 | -0.0022768 | 0 | 0.0071808 | 0 | 0.10092 | 931474.1817 | 232415.2946 | 0 | 0 | 0 | 106353.529 | 15879263.6105 | 0 | 0 | 0 | 117375.6661 | 118283403.9322 | 1168848.1432 | -795943.4169 | 0 | 1384839.7699 | -26483.6917 | 0 | 186239.9129 | 0 | 71452.3363

## Tower Properties
Location | Height [m] | OD [m] | Thickness [mm] | Mass Density [kg/m] | Fore-aft inertia [kg.m] | Side-side inertia [kg.m] | Fore-aft stiffness [N.m^2] | Side-side stiffness [N.m^2] | Torsional stiffness [N.m^2] | Axial stiffness [N]
Monopile start | -75 | 10 | 55.341 | 14429.9608 | 166718.8199 | 166718.8199 | 4.2748e+12 | 4.2748e+12 | 3.3899e+12 | 345793453239.6111
Mud line | -30 | 10 | 55.341 | 14429.9608 | 166718.8199 | 166718.8199 | 4.2748e+12 | 4.2748e+12 | 3.3899e+12 | 345793453239.6111
| -29.999 | 10 | 55.341 | 14429.9608 | 166718.8199 | 166718.8199 | 4.2748e+12 | 4.2748e+12 | 3.3899e+12 | 345793453239.6111
| -20 | 10 | 55.341 | 14429.9608 | 166718.8199 | 166718.8199 | 4.2748e+12 | 4.2748e+12 | 3.3899e+12 | 345793453239.6111
| -19.999 | 10 | 51.509 | 13435.9563 | 155353.4432 | 155353.4432 | 3.9834e+12 | 3.9834e+12 | 3.1589e+12 | 321973551662.2469
| -10 | 10 | 51.509 | 13435.9563 | 155353.4432 | 155353.4432 | 3.9834e+12 | 3.9834e+12 | 3.1589e+12 | 321973551662.2469
| -9.999 | 10 | 47.517 | 12399.6296 | 143485.4073 | 143485.4073 | 3.6791e+12 | 3.6791e+12 | 2.9175e+12 | 297139457640.3081
Water line | 0 | 10 | 47.517 | 12399.6296 | 143485.4073 | 143485.4073 | 3.6791e+12 | 3.6791e+12 | 2.9175e+12 | 297139457640.3081
| 0.001 | 10 | 43.527 | 11362.987 | 131594.6051 | 131594.6051 | 3.3742e+12 | 3.3742e+12 | 2.6758e+12 | 272297794747.5821
| 10 | 10 | 43.527 | 11362.987 | 131594.6051 | 131594.6051 | 3.3742e+12 | 3.3742e+12 | 2.6758e+12 | 272297794747.5821
| 10.001 | 10 | 41.058 | 10721.0975 | 124222.2152 | 124222.2152 | 3.1852e+12 | 3.1852e+12 | 2.5259e+12 | 256915828495.4436
Tower start | 15 | 10 | 41.058 | 10721.0975 | 124222.2152 | 124222.2152 | 3.1852e+12 | 3.1852e+12 | 2.5259e+12 | 256915828495.4436
| 15.001 | 10 | 39.496 | 10314.8444 | 119552.4206 | 119552.4206 | 3.0654e+12 | 3.0654e+12 | 2.4309e+12 | 247180551443.4128
| 28 | 10 | 39.496 | 10314.8444 | 119552.4206 | 119552.4206 | 3.0654e+12 | 3.0654e+12 | 2.4309e+12 | 247180551443.4128
| 28.001 | 10 | 36.456 | 9523.8185 | 110451.3039 | 110451.3039 | 2.8321e+12 | 2.8321e+12 | 2.2458e+12 | 228224743138.6868
| 41 | 9.926 | 36.456 | 9453.0844 | 108008.5676 | 108008.5676 | 2.7695e+12 | 2.7695e+12 | 2.1962e+12 | 226529700592.3543
| 41.001 | 9.926 | 33.779 | 8761.3061 | 100158.4907 | 100158.4907 | 2.5682e+12 | 2.5682e+12 | 2.0366e+12 | 209952218050.8469
| 54 | 9.443 | 33.779 | 8333.5244 | 86192.1833 | 86192.1833 | 2.2101e+12 | 2.2101e+12 | 1.7526e+12 | 199701039744.324
| 54.001 | 9.443 | 32.192 | 7943.3395 | 82184.1879 | 82184.1879 | 2.1073e+12 | 2.1073e+12 | 1.6711e+12 | 190350814904.366
| 67 | 8.833 | 32.192 | 7428.4595 | 67216.5004 | 67216.5004 | 1.7235e+12 | 1.7235e+12 | 1.3667e+12 | 178012448518.4323
| 67.001 | 8.833 | 30.708 | 7087.2142 | 64150.2894 | 64150.2894 | 1.6449e+12 | 1.6449e+12 | 1.3044e+12 | 169834990660.5962
| 80 | 8.151 | 30.708 | 6538.0981 | 50364.8066 | 50364.8066 | 1.2914e+12 | 1.2914e+12 | 1.0241e+12 | 156676206149.6397
| 80.001 | 8.151 | 29.101 | 6197.1749 | 47757.4061 | 47757.4061 | 1.2245e+12 | 1.2245e+12 | 971067257127.3551 | 148506466847.5468
| 93 | 7.39 | 29.101 | 5616.5163 | 35551.814 | 35551.814 | 911584975111.2295 | 911584975111.2295 | 722886885263.205 | 134591812002.5436
| 93.001 | 7.39 | 27.213 | 5253.4779 | 33270.8237 | 33270.8237 | 853098044023.8868 | 853098044023.8868 | 676506748910.9423 | 125892114148.985
| 106 | 6.909 | 27.213 | 4910.276 | 27166.9811 | 27166.9811 | 696589258960.8757 | 696589258960.8757 | 552395282355.9745 | 117667768272.1226
| 106.001 | 6.909 | 24.009 | 4334.1676 | 24001.8088 | 24001.8088 | 615430994795.9966 | 615430994795.9966 | 488036778873.2252 | 103862152005.8945
| 119 | 6.748 | 24.009 | 4232.8166 | 22357.0999 | 22357.0999 | 573258971811.3063 | 573258971811.3063 | 454594364646.3658 | 101433418769.6498
| 119.001 | 6.748 | 20.826 | 3673.3878 | 19420.5935 | 19420.5935 | 497963935464.2214 | 497963935464.2214 | 394885400823.1276 | 88027505148.3052
| 132 | 6.572 | 20.826 | 3577.2826 | 17935.8575 | 17935.8575 | 459893782098.6934 | 459893782098.6934 | 364695769204.2639 | 85724481485.4559
| 132.001 | 6.572 | 23.998 | 4120.1413 | 20637.7231 | 20637.7231 | 529172386815.796 | 529172386815.796 | 419633702744.9262 | 98733315436.6877
Tower top | 144.386 | 6.5 | 23.998 | 4074.8373 | 19964.4074 | 19964.4074 | 511907882162.8501 | 511907882162.8501 | 405942950555.1401 | 97647671493.4752

## Floating Tower Properties
Location | Height [m] | OD [m] | Thickness [mm] | Mass Density [kg/m] | Fore-aft inertia [kg.m] | Side-side inertia [kg.m] | Fore-aft stiffness [N.m^2] | Side-side stiffness [N.m^2] | Torsional stiffness [N.m^2] | Axial stiffness [N]
Tower start | 15 | 10 | 88.528 | 23006.3151 | 264048.8391 | 264048.8391 | 6.7705e+12 | 6.7705e+12 | 5.369e+12 | 551313566622.5398
| 28 | 10 | 88.528 | 23006.3151 | 264048.8391 | 264048.8391 | 6.7705e+12 | 6.7705e+12 | 5.369e+12 | 551313566622.5398
| 28.001 | 10 | 78.377 | 20389.173 | 234486.7934 | 234486.7934 | 6.0125e+12 | 6.0125e+12 | 4.7679e+12 | 488597482908.2112
| 41 | 10 | 78.377 | 20389.173 | 234486.7934 | 234486.7934 | 6.0125e+12 | 6.0125e+12 | 4.7679e+12 | 488597482908.2112
| 41.001 | 10 | 68.146 | 17745.9375 | 204506.1076 | 204506.1076 | 5.2437e+12 | 5.2437e+12 | 4.1583e+12 | 425256111771.0334
| 54 | 10 | 68.146 | 17745.9375 | 204506.1076 | 204506.1076 | 5.2437e+12 | 5.2437e+12 | 4.1583e+12 | 425256111771.0334
| 54.001 | 10 | 57.782 | 15062.7443 | 173944.8487 | 173944.8487 | 4.4601e+12 | 4.4601e+12 | 3.5369e+12 | 360957208940.9086
| 67 | 10 | 57.782 | 15062.7443 | 173944.8487 | 173944.8487 | 4.4601e+12 | 4.4601e+12 | 3.5369e+12 | 360957208940.9086
| 67.001 | 10 | 47.297 | 12342.4931 | 142830.5222 | 142830.5222 | 3.6623e+12 | 3.6623e+12 | 2.9042e+12 | 295770263019.2291
| 80 | 10 | 47.297 | 12342.4931 | 142830.5222 | 142830.5222 | 3.6623e+12 | 3.6623e+12 | 2.9042e+12 | 295770263019.2291
| 80.001 | 10 | 36.876 | 9633.1339 | 111709.6911 | 111709.6911 | 2.8644e+12 | 2.8644e+12 | 2.2714e+12 | 230844329108.8167
| 93 | 10 | 36.876 | 9633.1339 | 111709.6911 | 111709.6911 | 2.8644e+12 | 2.8644e+12 | 2.2714e+12 | 230844329108.8167
| 93.001 | 10 | 26.873 | 7027.0939 | 81652.1909 | 81652.1909 | 2.0936e+12 | 2.0936e+12 | 1.6603e+12 | 168394293425.278
| 106 | 10 | 26.873 | 7027.0939 | 81652.1909 | 81652.1909 | 2.0936e+12 | 2.0936e+12 | 1.6603e+12 | 168394293425.278
| 106.001 | 10 | 17.749 | 4645.4804 | 54077.326 | 54077.326 | 1.3866e+12 | 1.3866e+12 | 1.0996e+12 | 111322318714.7265
| 119 | 10 | 17.749 | 4645.4804 | 54077.326 | 54077.326 | 1.3866e+12 | 1.3866e+12 | 1.0996e+12 | 111322318714.7265
| 119.001 | 10 | 9.911 | 2596.0622 | 30267.7727 | 30267.7727 | 776096735821.6012 | 776096735821.6012 | 615444711506.5297 | 62210931156.458
| 132 | 10 | 9.911 | 2596.0622 | 30267.7727 | 30267.7727 | 776096735821.6012 | 776096735821.6012 | 615444711506.5297 | 62210931156.458
| 132.001 | 10 | 7.936 | 2079.1466 | 24250.5751 | 24250.5751 | 621809618496.835 | 621809618496.835 | 493095027467.9901 | 49823787036.3944
Tower top | 144.386 | 6.5 | 7.936 | 1350.8673 | 6651.2791 | 6651.2791 | 170545618767.4217 | 170545618767.4217 | 135242675682.5654 | 32371611527.1717

## Material Properties
Material name | Density [kg/m^3] | Fiber vol fraction | Young Modulus E_1 [MPa] | Young Modulus E_2 [MPa] | Young Modulus E_3 [MPa] | Shear Modulus G_1 [MPa] | Shear Modulus G_2 [MPa] | Shear Modulus G_3 [MPa] | Poisson ratio nu_1 | Poisson ratio nu_2 | Poisson ratio nu_3 | Tensile failure Xt_1 [MPa] | Tensile failure Xt_2 [MPa] | Tensile failure Xt_3 [MPa] | Compressive failure Xc_1 [MPa] | Compressive failure Xc_2 [MPa] | Compressive failure Xc_3 [MPa] | Description | Reference
Gelcoat | 1235 |  | 3440 | 3440 | 3440 | 1323 | 1323 | 1323 | 0.3 | 0.3 | 0.3 | 74 | 74 | 74 | 87 | 87 | 87
steel | 7800 |  | 200000 | 200000 | 200000 | 79300 | 79300 | 79300 | 0.3 | 0.3 | 0.3 | 450 | 450 | 450 | 450 | 450 | 450 | Steel of the tower and monopile ASTM A572 Grade 50 | http://www.matweb.com/search/DataSheet.aspx?MatGUID=9ced5dc901c54bd1aef19403d0385d7f
steel_drive | 7850 |  | 205000 | 205000 | 205000 | 80000 | 80000 | 80000 | 0.3 | 0.3 | 0.3 | 814 | 814 | 814 | 814 | 814 | 814 | Steel of the drivetrain ASTM 4140 40Cr1Mo28 | http://www.matweb.com/search/DataSheet.aspx?MatGUID=38108bfd64c44b4c9c6a02af78d5b6c6
cast_iron | 7200 |  | 118000 | 118000 | 118000 | 47600 | 47600 | 47600 | 0.3 | 0.3 | 0.3 | 310 | 310 | 310 | 310 | 310 | 310 | Cast iron for hub and nacelle components | TODO
glass_uni | 1940 | 0.57 | 44600 | 17000 | 16700 | 3270 | 3480 | 3500 | 0.262 | 0.35 | 0.264 | 609.2 | 38.1 | 15.29 | 474.71 | 112.64 | 113.22 | Vectorply E-LT-5500, Epikote MGS RIMR 135/Epicure MGS RIMH 1366 epoxy | MSU composites database 3D property tests, Engineering Mechanics of Composite Materials, Daniel, I & Ishai, O., 1994, pg. 34
CarbonUD | 1220 | 0.10769 | 114500 | 8390 | 8390 | 5990 | 5990 | 5990 | 0.27 | 0.27 | 0.27 | 1546 | 0 | 0 | 1047 | 0 | 0
glass_biax | 1940 | 0.57 | 11100 | 11100 | 16700 | 13530 | 3490 | 3490 | 0.5 | 0 | 0.066 | 42.9 | 42.6 | 15.3 | 70.7 | 70.7 | 113.2 | Vectorply E-LT-5500, Epikote MGS RIMR 135/Epicure MGS RIMH 1366 epoxy | MSU composites database 3D property tests, Engineering Mechanics of Composite Materials, Daniel, I & Ishai, O., 1994, pg. 34
glass_triax | 1940 | 0.57 | 28700 | 16600 | 16700 | 8400 | 3490 | 3490 | 0.5 | 0 | 0.17 | 396 | 76.4 | 15.3 | 448.9 | 174.7 | 113.2 | Vectorply E-LT-5500, Epikote MGS RIMR 135/Epicure MGS RIMH 1366 epoxy | MSU composites database 3D property tests, Engineering Mechanics of Composite Materials, Daniel, I & Ishai, O., 1994, pg. 34
medium_density_foam | 130 |  | 129.2 | 129.2 | 129.2 | 48.947 | 48.947 | 48.947 | 0.32 | 0.32 | 0.32 | 2.083 | 2.083 | 2.083 | 1.563 | 1.563 | 1.563 | Airex C70.130 PVC Foam, source 'https://www.3accorematerials.com/uploads/documents/TDS-AIREX-C70-E_1106.pdf'
resin | 1150 |  | 1 | 1 | 1 | 0.3125 | 0.3125 | 0.3125 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | epoxy
adhesive | 1100 |  | 4.56 | 4.56 | 4.56 | 1.52 | 1.52 | 1.52 | 0.49 | 0.49 | 0.49 | 0.69 | 0.69 | 0.69 | 0.4 | 0.4 | 0.4 | Sample adhesive | https://www.nrel.gov/docs/fy19osti/73585.pdf

## Rotor Performance
Wind [m/s] | Pitch [deg] | Power [MW] | Power Coefficient [-] | Aero Power Coefficient [-] | Rotor Speed [rpm] | Tip Speed [m/s] | Thrust [MN] | Thrust Coefficient [-] | Torque [MNm] | Torque Coefficient [-] | Blade Moment [MNm] | Blade Moment Coefficient [-]
3 | 3.9249 | 0.042733 | 0.056744 | 0.059303 | 5 | 63.4177 | 0.20269 | 0.80742 | 0.085295 | 0.0028222 | 5.9719 | 0.19759
3.5495 | 3.9154 | 0.29259 | 0.23456 | 0.24514 | 5 | 63.4177 | 0.27574 | 0.78466 | 0.584 | 0.013803 | 7.8507 | 0.18556
4.0679 | 3.7071 | 0.60797 | 0.32381 | 0.33841 | 5 | 63.4177 | 0.36083 | 0.78177 | 1.2135 | 0.021837 | 10.0484 | 0.18083
4.5539 | 3.3458 | 0.9811 | 0.37246 | 0.38925 | 5 | 63.4177 | 0.45428 | 0.78538 | 1.9583 | 0.028119 | 12.4676 | 0.17903
5.0064 | 2.9054 | 1.402 | 0.40057 | 0.41863 | 5 | 63.4177 | 0.55092 | 0.78805 | 2.7983 | 0.033247 | 14.9717 | 0.17788
5.4244 | 2.4105 | 1.8587 | 0.41751 | 0.43633 | 5 | 63.4177 | 0.64829 | 0.78992 | 3.7099 | 0.037546 | 17.4991 | 0.1771
5.8069 | 1.8943 | 2.3376 | 0.42801 | 0.44731 | 5 | 63.4177 | 0.74345 | 0.79046 | 4.6658 | 0.041204 | 19.9729 | 0.17638
6.153 | 1.3803 | 2.8241 | 0.43464 | 0.45424 | 5 | 63.4177 | 0.83409 | 0.78987 | 5.6368 | 0.044337 | 22.3335 | 0.17567
6.4619 | 0.88173 | 3.3031 | 0.43888 | 0.45867 | 5 | 63.4177 | 0.91862 | 0.78873 | 6.5929 | 0.047017 | 24.5403 | 0.17501
6.733 | 0.41226 | 3.7594 | 0.44159 | 0.4615 | 5 | 63.4177 | 0.99556 | 0.78736 | 7.5038 | 0.049291 | 26.5548 | 0.17444
6.9655 | -0.014525 | 4.1786 | 0.4433 | 0.46329 | 5 | 63.4177 | 1.0635 | 0.7859 | 8.3405 | 0.051191 | 28.3404 | 0.17394
7.1589 | 0 | 4.5472 | 0.44434 | 0.46365 | 5.0861 | 64.5096 | 1.1125 | 0.77828 | 8.9085 | 0.051763 | 29.6215 | 0.17211
7.3128 | 0 | 4.8553 | 0.44512 | 0.46365 | 5.1954 | 65.8967 | 1.1609 | 0.77828 | 9.2957 | 0.051763 | 30.9091 | 0.17211
7.4269 | 0 | 5.0915 | 0.4456 | 0.46365 | 5.2765 | 66.9246 | 1.1974 | 0.77828 | 9.588 | 0.051763 | 31.8809 | 0.17211
7.5009 | 0 | 5.2485 | 0.44588 | 0.46365 | 5.329 | 67.5909 | 1.2213 | 0.77828 | 9.7799 | 0.051763 | 32.5189 | 0.17211
7.5345 | 0 | 5.3208 | 0.44599 | 0.46365 | 5.3529 | 67.8941 | 1.2323 | 0.77828 | 9.8678 | 0.051763 | 32.8113 | 0.17211
7.5412 | 0 | 5.3353 | 0.44602 | 0.46365 | 5.3577 | 67.9547 | 1.2345 | 0.77828 | 9.8855 | 0.051763 | 32.8699 | 0.17211
7.5883 | 0 | 5.4379 | 0.44618 | 0.46365 | 5.3912 | 68.3791 | 1.25 | 0.77828 | 10.0093 | 0.051763 | 33.2817 | 0.17211
7.6757 | 0 | 5.6313 | 0.44645 | 0.46365 | 5.4532 | 69.1662 | 1.2789 | 0.77828 | 10.241 | 0.051763 | 34.0523 | 0.17211
7.8031 | 0 | 5.921 | 0.4468 | 0.46365 | 5.5437 | 70.3141 | 1.3217 | 0.77828 | 10.5838 | 0.051763 | 35.192 | 0.17211
7.9702 | 0 | 6.3151 | 0.44719 | 0.46365 | 5.6625 | 71.8203 | 1.379 | 0.77828 | 11.0421 | 0.051763 | 36.7158 | 0.17211
8.1767 | 0 | 6.8245 | 0.44756 | 0.46365 | 5.8092 | 73.6813 | 1.4514 | 0.77828 | 11.6217 | 0.051763 | 38.6432 | 0.17211
8.4221 | 0 | 7.4628 | 0.44787 | 0.46365 | 5.9836 | 75.8927 | 1.5398 | 0.77828 | 12.3298 | 0.051763 | 40.9976 | 0.17211
8.7059 | 0 | 8.2384 | 0.44763 | 0.46365 | 6.1851 | 78.4494 | 1.6453 | 0.77828 | 13.1746 | 0.051763 | 43.8065 | 0.17211
9.0273 | 0 | 9.168 | 0.44681 | 0.46365 | 6.4135 | 81.3456 | 1.769 | 0.77828 | 14.1653 | 0.051763 | 47.1007 | 0.17211
9.3856 | 0 | 10.2852 | 0.44601 | 0.46365 | 6.6681 | 84.5745 | 1.9122 | 0.77828 | 15.3121 | 0.051763 | 50.9141 | 0.17211
9.78 | 0 | 11.6172 | 0.44525 | 0.46365 | 6.9483 | 88.1287 | 2.0763 | 0.77828 | 16.6262 | 0.051763 | 55.2833 | 0.17211
10.2096 | 0 | 13.1944 | 0.4445 | 0.46365 | 7.2535 | 92 | 2.2628 | 0.77828 | 18.1189 | 0.051763 | 60.2468 | 0.17211
10.6585 | 3.0358e-18 | 15 | 0.44415 | 0.46383 | 7.4992 | 95.117 | 2.4454 | 0.77176 | 19.947 | 0.052287 | 65.0641 | 0.17055
10.6735 | 0.50274 | 15 | 0.44228 | 0.46188 | 7.4992 | 95.117 | 2.3741 | 0.74715 | 19.947 | 0.05214 | 63.0316 | 0.16476
11.1704 | 3.7223 | 15 | 0.38584 | 0.40294 | 7.4992 | 95.117 | 1.9571 | 0.56234 | 19.947 | 0.047604 | 50.8819 | 0.12143
11.6993 | 5.3975 | 15 | 0.33584 | 0.35072 | 7.4992 | 95.117 | 1.7694 | 0.46348 | 19.947 | 0.043398 | 45.1918 | 0.098321
12.2589 | 6.769 | 15 | 0.29191 | 0.30485 | 7.4992 | 95.117 | 1.6309 | 0.38908 | 19.947 | 0.039526 | 40.8725 | 0.08099
12.848 | 7.9927 | 15 | 0.25357 | 0.26481 | 7.4992 | 95.117 | 1.5186 | 0.32982 | 19.947 | 0.035984 | 37.2739 | 0.067242
13.4652 | 9.1278 | 14.9999 | 0.22028 | 0.23004 | 7.4992 | 95.117 | 1.4234 | 0.28147 | 19.9469 | 0.032761 | 34.1436 | 0.056078
14.109 | 10.2039 | 15.0001 | 0.19148 | 0.19996 | 7.4992 | 95.117 | 1.3409 | 0.24149 | 19.9471 | 0.029839 | 31.353 | 0.046902
14.7781 | 11.2379 | 15.0001 | 0.16663 | 0.17402 | 7.4992 | 95.117 | 1.2681 | 0.20818 | 19.9471 | 0.027199 | 28.8245 | 0.039304
15.4707 | 12.2399 | 15 | 0.14524 | 0.15167 | 7.4992 | 95.117 | 1.2034 | 0.18026 | 19.9471 | 0.024818 | 26.5089 | 0.032982
16.1854 | 13.2167 | 15 | 0.12683 | 0.13246 | 7.4992 | 95.117 | 1.1453 | 0.15675 | 19.947 | 0.022674 | 24.3718 | 0.027704
16.9205 | 14.1724 | 15 | 0.11101 | 0.11593 | 7.4992 | 95.117 | 1.0931 | 0.13688 | 19.947 | 0.020747 | 22.3878 | 0.023286
17.6743 | 15.11 | 15 | 0.097406 | 0.10172 | 7.4992 | 95.117 | 1.0458 | 0.12003 | 19.947 | 0.019015 | 20.5376 | 0.019578
18.4449 | 16.0313 | 15 | 0.0857 | 0.089498 | 7.4992 | 95.117 | 1.0029 | 0.10569 | 19.947 | 0.017459 | 18.8059 | 0.016461
19.2308 | 16.9377 | 15 | 0.075617 | 0.078968 | 7.4992 | 95.117 | 0.96399 | 0.093454 | 19.947 | 0.016062 | 17.1802 | 0.013834
20.0299 | 17.8297 | 15 | 0.066922 | 0.069888 | 7.4992 | 95.117 | 0.92857 | 0.08298 | 19.947 | 0.014806 | 15.6499 | 0.011616
20.8406 | 18.7077 | 15 | 0.059413 | 0.062046 | 7.4992 | 95.117 | 0.8963 | 0.073986 | 19.947 | 0.013676 | 14.2064 | 0.0097402
21.6609 | 19.5718 | 14.9999 | 0.052915 | 0.05526 | 7.4992 | 95.117 | 0.86689 | 0.066241 | 19.9468 | 0.01266 | 12.8422 | 0.0081506
22.4889 | 20.4215 | 15 | 0.047283 | 0.049379 | 7.4992 | 95.117 | 0.84007 | 0.059552 | 19.947 | 0.011745 | 11.5515 | 0.0068016
23.3227 | 21.2565 | 15 | 0.042391 | 0.04427 | 7.4992 | 95.117 | 0.81559 | 0.053757 | 19.947 | 0.01092 | 10.3284 | 0.0056543
24.1604 | 22.0764 | 15 | 0.038133 | 0.039823 | 7.4992 | 95.117 | 0.79325 | 0.048722 | 19.947 | 0.010176 | 9.1684 | 0.0046773
25 | 22.8807 | 15 | 0.034418 | 0.035944 | 7.4992 | 95.117 | 0.77286 | 0.044334 | 19.947 | 0.0095039 | 8.0673 | 0.0038437

## Nacelle Mass Properties
| Mass | CoM_TT_x | CoM_TT_y | CoM_TT_z | MoI_CoM_xx | MoI_CoM_yy | MoI_CoM_zz | MoI_CoM_xy | MoI_CoM_xz | MoI_CoM_yz | MoI_TT_xx | MoI_TT_yy | MoI_TT_zz | MoI_TT_xy | MoI_TT_xz | MoI_TT_yz
Component
mb1 | 48092.0018 | -6.094 | 0 | 4.99 | 62609.7748 | 32777.705 | 32777.705 | 0 | 0 | 0 | 1259762.7145 | 3016243.8905 | 1819090.9508 | 0 | 1459322.1423 | 0
mb2 | 13479.2839 | -5.0995 | 0 | 4.8854 | 17548.3427 | 9186.9744 | 9186.9744 | 0 | 0 | 0 | 339173.6697 | 681428.6711 | 359803.344 | 0 | 334942.8545 | 0
lss | 21455.507 | -6.5913 | 0 | 5.0422 | 45163.8423 | 38673.5514 | 38673.5514 | 0 | 0 | 0 | 590579.3774 | 1516289.7268 | 970874.1917 | 0 | 712392.0075 | 0
hss | 0 | -4.8011 | 0 | 4.8541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
brake | 24335.3438 | -7.0885 | 0 | 5.0945 | 17849.7102 | 8924.8551 | 8924.8551 | 0 | 0 | 0 | 649348.409 | 1863304.039 | 1231805.3403 | 0 | 877881.1156 | 0
gearbox | 0 | -4.8011 | 0 | 4.8541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
generator_rotor | 130349.2496 | -6.0194 | 0 | 4.9821 | 1836783.8456 | 972876.6339 | 972876.6339 | 0 | 0 | 0 | 5062818.1548 | 8931341.2784 | 5705306.9692 | 0 | 3819298.1813 | 0
generator_stator | 238490.1575 | -6.0194 | 0 | 4.9821 | 3360624.3988 | 1779998.7521 | 1779998.7521 | 0 | 0 | 0 | 9263055.2357 | 16340999.2342 | 10438568.3973 | 0 | 6987880.8469 | 0
generator | 368839.4072 | -6.0194 | 0 | 4.9821 | 5197408.2444 | 2752875.3861 | 2752875.3861 | 0 | 0 | 0 | 14325873.3905 | 25272340.5127 | 16143875.3665 | 0 | 10807179.0282 | 0
hvac | 9381.2812 | -6.0194 | 0 | 4.9821 | 148718.225 | 74359.1125 | 74359.1125 | 0 | 0 | 0 | 380763.9277 | 647132.605 | 415086.9023 | 0 | 273609.6936 | 0
nose | 6732.5901 | -5.4476 | 0 | 4.922 | 7439.5121 | 4667.9292 | 4667.9292 | 0 | 0 | 0 | 170514.9532 | 367569.7624 | 204494.3213 | 0 | 180233.0373 | 0
bedplate | 41606.3054 | -1.2573 | 0 | 2.606 | 542794.3243 | 649566.1506 | 391772.3182 | 0 | 170516.0332 | 0 | 825349.1166 | 997894.6618 | 457546.0371 | 0 | 306841.6708 | 0
platform | 48672 | 0 | 0 | 0 | 685470.4896 | 685470.4896 | 1370928 | 0 | 0 | 0 | 685470.4896 | 685470.4896 | 1370928 | 0 | 0 | 0
cover | 20157.7167 | -0.24006 | 0 | 5.8396 | 1568.1605 | 1138.2673 | 1138.2673 | 0 | 0 | 0 | 688962.9235 | 689694.6595 | 2299.8965 | 0 | 28257.7039 | 0
transformer | 30635 | 0 | -5.0668 | 1.8168 | 67411.3188 | 67411.3188 | 67411.3188 | 0 | 0 | 0 | 954998.954 | 168528.2969 | 853881.9758 | 0 | 0 | 282002.7238
converter | 11983.85 | 0 | 5.0668 | 1.8168 | 26370.0712 | 26370.0712 | 26370.0712 | 0 | 0 | 0 | 373578.0713 | 65925.1781 | 334022.9644 | 0 | 0 | -110314.2922
Above_yaw | 645370.2871 | -4.7201 | -0.14643 | 4.2751 | 9435311.1637 | 9798039.6063 | 9771315.6464 | 446057.746 | 1957666.8664 | -232316.4414 | 21244375.997 | 35971822.4933 | 24163709.2907 | 1.7462e-10 | 14980659.2536 | 171688.4316
yaw | 28279.9261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
nacelle | 673650.2132 | -4.522 | -0.14028 | 4.0957 | 9910245.7964 | 10850691.6273 | 10350146.0861 | 428118.2838 | 2481422.9973 | -216068.2534 | 21223564.5085 | 35925695.6078 | 24138345.1202 | 786.1017 | 14957708.4222 | 170976.4411
Blades | 204961.4117 | -11.4202 | 0 | 5.5498 | 349224644.6432 | 174612322.3216 | 174612322.3216 | 0 | 0 | 0 | 353629606.0426 | 207656555.9477 | 203251594.5483 | 0 | -5161574.8091 | 0
Hub_System | 69112.6905 | -11.4202 | 0 | 5.5498 | 969656.6411 | 618004.0647 | 618004.0647 | 0 | 0 | 0 | 3094484.9488 | 11760471.6759 | 9635643.3682 | 0 | 4343786.5952 | 0
RNA | 947724.3153 | -6.5169 | -0.099714 | 4.5162 | 477786152.0464 | 314940913.4691 | 315943964.7992 | 616641.0076 | -13752941.9304 | -255807.9433 | 377947655.4998 | 255342723.2314 | 237025583.0367 | 786.1017 | 14139920.2083 | 170976.4411